## Sheet1
Table ( B1 ) Sanitary Sewer Design Report For ( Line Road A)
Manhole Report | [6 empty] | Pipe Report
Label | Ground Elevation (m) | Invert Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | X coordinate (m) | Y coordinate (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (m³/day) | Section Shape | Section Size (in) | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 845.68 | 840.82 | 1.2 | 4.85 | 156872.79 | 101813.74 | CO-1 | MH-1 | MH-2 | 50.3 | 37.53 | Circular | 8 | 0.64 | 0.05 | 3.4 | PVC
MH-2 | 840.71 | 838.31 | 1.2 | 2.4 | 156833.28 | 101844.81 | CO-2 | MH-2 | MH-3 | 50.2 | 65.52 | Circular | 8 | 0.75 | 0.05 | 2.1 | PVC
MH-3 | 838 | 835.8 | 1.2 | 2.2 | 156793.81 | 101875.83 | CO-3 | MH-3 | MH-4 | 50.1 | 94.73 | Circular | 8 | 0.85 | 0.05 | 2.2 | PVC
MH-4 | 836 | 833.3 | 1.2 | 2.7 | 156754.47 | 101906.77 | CO-4 | MH-4 | MH-5 | 50.3 | 125.22 | Circular | 8 | 0.92 | 0.05 | 1.8 | PVC
MH-5 | 832 | 830.8 | 1.2 | 1.2 | 156714.92 | 101937.88 | CO-5 | MH-5 | MH-6 | 50 | 169.88 | Circular | 8 | 0.67 | 0.016 | 1 | PVC
MH-6 | 831.2 | 830 | 1.2 | 1.2 | 156658.31 | 101982.3 | CO-6 | MH-6 | MH-7 | 50 | 209.64 | Circular | 8 | 0.92 | 0.032 | 1 | PVC
MH-7 | 829.6 | 828.4 | 1.2 | 1.2 | 156607.3 | 102001.37 | CO-7 | MH-7 | MH-8 | 50 | 249.17 | Circular | 8 | 1.06 | 0.042 | 1 | PVC
MH-8 | 827.3 | 826.1 | 1.2 | 1.2 | 156556.14 | 102020.18 | CO-8 | MH-8 | MH-9 | 50 | 288.53 | Circular | 8 | 0.77 | 0.015 | 1 | PVC
MH-9 | 826.5 | 825.3 | 1.2 | 1.2 | 156505.25 | 102038.83 | CO-9 | MH-9 | MH-10 | 50 | 327.78 | Circular | 8 | 1.18 | 0.044 | 1 | PVC
MH-10 | 824.1 | 822.9 | 1.2 | 1.2 | 156454.51 | 102057.57 | CO-10 | MH-10 | MH-11 | 41 | 357.24 | Circular | 8 | 1.18 | 0.041 | 1 | PVC
MH-11 | 822.4 | 821.2 | 1.2 | 1.2 | 156416.08 | 102071.78 | CO-11 | MH-11 | MH-12 | 50.1 | 391.85 | Circular | 8 | 1 | 0.024 | 1 | PVC
MH-12 | 821.2 | 820 | 1.2 | 1.2 | 156371.39 | 102094.36 | CO-12 | MH-12 | MH-13 | 50 | 428.11 | Circular | 8 | 1.08 | 0.028 | 1 | PVC
MH-13 | 819.8 | 818.6 | 1.2 | 1.2 | 156326.76 | 102116.9 | CO-13 | MH-13 | MH-14 | 50.2 | 466.02 | Circular | 8 | 0.91 | 0.016 | 1.2 | PVC
MH-14 | 819.39 | 817.81 | 1.2 | 1.58 | 156281.96 | 102139.54 | CO-14 | MH-14 | MH-15 | 50.1 | 505.56 | Circular | 8 | 1.4 | 0.05 | 2 | PVC
MH-15 | 818.1 | 815.31 | 1.2 | 2.79 | 156237.29 | 102162.14 | CO-15 | MH-15 | MH-16 | 50.1 | 546.76 | Circular | 8 | 1.43 | 0.05 | 2.3 | PVC
MH-16 | 815 | 812.8 | 1.2 | 2.2 | 156192.53 | 102184.71 | CO-16 | MH-16 | MH-17 | 50.1 | 589.61 | Circular | 8 | 1.46 | 0.05 | 1.7 | PVC
MH-17 | 811.9 | 810.29 | 1.2 | 1.61 | 156147.81 | 102207.3 | CO-17 | MH-17 | MH-18 | 50 | 634.1 | Circular | 8 | 1.49 | 0.05 | 1.2 | PVC
MH-18 | 809 | 807.8 | 1.2 | 1.2 | 156103.25 | 102229.9 | CO-18 | MH-18 | MH-19 | 50 | 687.05 | Circular | 8 | 1.1 | 0.02 | 1.2 | PVC
MH-19 | 808.3 | 806.8 | 1.2 | 1.5 | 156052.08 | 102255.56 | CO-19 | MH-19 | MH-20 | 50.4 | 741.16 | Circular | 8 | 1.56 | 0.05 | 1.5 | PVC
MH-20 | 806.25 | 804.3 | 1.2 | 1.95 | 156002.7 | 102269.89 | CO-20 | MH-20 | MH-21 | 51.6 | 797.14 | Circular | 8 | 1.59 | 0.05 | 1.9 | PVC
MH-21 | 804 | 801.8 | 1.2 | 2.2 | 155953.13 | 102284.19 | CO-21 | MH-21 | MH-22 | 49.6 | 856.74 | Circular | 8 | 1.63 | 0.05 | 2.2 | PVC
MH-22 | 801.9 | 799.3 | 1.2 | 2.6 | 155903.59 | 102298.5 | CO-22 | MH-22 | MH-23 | 51.3 | 919.6 | Circular | 8 | 1.66 | 0.05 | 1.7 | PVC
MH-23 | 798 | 796.8 | 1.2 | 1.2 | 155854.32 | 102312.68 | CO-23 | MH-23 | MH-24 | 51.6 | 987.25 | Circular | 8 | 1.57 | 0.04 | 1 | PVC
MH-24 | 796 | 794.8 | 1.2 | 1.2 | 155804.8 | 102327.01 | CO-24 | MH-24 | MH-25 | 51.4 | 1057.31 | Circular | 8 | 1.2 | 0.018 | 1 | PVC
MH-25 | 795.1 | 793.9 | 1.2 | 1.2 | 155755.4 | 102341.31 | CO-25 | MH-25 | MH-26 | 51.6 | 1128.08 | Circular | 8 | 1.32 | 0.022 | 1 | PVC
MH-26 | 794 | 792.78 | 1.2 | 1.22 | 155705.81 | 102355.67 | CO-26 | MH-26 | MH-27 | 41.7 | 1185.77 | Circular | 8 | 1.79 | 0.05 | 1 | PVC
MH-27 | 791.9 | 790.7 | 1.2 | 1.2 | 155665.75 | 102367.21 | CO-27 | MH-27 | MH-28 | 30.8 | 1228.91 | Circular | 8 | 1.49 | 0.029 | 1 | PVC
MH-28 | 791 | 789.8 | 1.2 | 1.2 | 155636.18 | 102375.73 | CO-28 | MH-28 | MH-29 | 50 | 1301.72 | Circular | 8 | 1.69 | 0.04 | 1 | PVC
MH-29 | 789 | 787.8 | 1.2 | 1.2 | 155586.52 | 102381.88 | CO-29 | MH-29 | MH-30 | 50.2 | 1375.33 | Circular | 8 | 1.55 | 0.03 | 1 | PVC
MH-30 | 787.5 | 786.3 | 1.2 | 1.2 | 155536.67 | 102388.05 | CO-30 | MH-30 | MH-31 | 50 | 1449.55 | Circular | 8 | 1.71 | 0.038 | 1 | PVC
MH-31 | 785.6 | 784.4 | 1.2 | 1.2 | 155487.02 | 102394.12 | CO-31 | MH-31 | MH-32 | 50.1 | 1524.58 | Circular | 8 | 1.8 | 0.042 | 1 | PVC
MH-32 | 783.5 | 782.3 | 1.2 | 1.2 | 155437.3 | 102400.17 | CO-32 | MH-32 | MH-33 | 50 | 1605.13 | Circular | 8 | 1.86 | 0.044 | 1 | PVC
MH-33 | 781.3 | 780.1 | 1.2 | 1.2 | 155384.51 | 102406.68 | CO-33 | MH-33 | MH-34 | 50.3 | 1682.92 | Circular | 8 | 1.91 | 0.046 | 1 | PVC
MH-34 | 779 | 777.8 | 1.2 | 1.2 | 155334.2 | 102408.32 | CO-34 | MH-34 | MH-35 | 43.6 | 1750.89 | Circular | 8 | 1.98 | 0.049 | 1 | PVC
MH-35 | 776.85 | 775.65 | 1.2 | 1.2 | 155290.65 | 102409.75 | CO-35 | MH-35 | MH-36 | 50 | 4136.24 | Circular | 8 | 2.05 | 0.031 | 1 | PVC
Table ( B1.1 ) Sanitary Sewer Design Report For ( Line Road A)
Manhole Report | [6 empty] | Pipe Report
Label | Ground Elevation (m) | Invert Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | X coordinate (m) | Y coordinate (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (m³/day) | Section Shape | Section Size (in) | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-36 | 775.32 | 774.12 | 1.2 | 1.2 | 155250.19 | 102444.54 | CO-36 | MH-36 | MH-37 | 50 | 4200.19 | Circular | 10 | 1.72 | 0.02 | 1 | PVC
MH-37 | 774.35 | 773.1 | 1.2 | 1.25 | 155210.35 | 102479.47 | CO-37 | MH-37 | MH-38 | 50 | 4264.14 | Circular | 10 | 1.96 | 0.027 | 1.1 | PVC
MH-38 | 773 | 771.75 | 1.2 | 1.25 | 155169.98 | 102514.75 | CO-38 | MH-38 | MH-39 | 49 | 4326.95 | Circular | 10 | 2.31 | 0.04 | 1.7 | PVC
MH-39 | 772.3 | 769.66 | 1.2 | 2.64 | 155131.39 | 102550.32 | CO-39 | MH-39 | MH-40 | 50 | 4405.27 | Circular | 10 | 2.53 | 0.05 | 2.1 | PVC
MH-40 | 769.3 | 767.16 | 1.2 | 2.14 | 155082.93 | 102594.58 | CO-40 | MH-40 | MH-41 | 50.3 | 4452.59 | Circular | 10 | 2.53 | 0.05 | 1.4 | PVC
MH-41 | 765.9 | 764.65 | 1.2 | 1.25 | 155054.02 | 102635.76 | CO-41 | MH-41 | MH-42 | 50.3 | 4500.19 | Circular | 10 | 2.5 | 0.048 | 1 | PVC
MH-42 | 763.5 | 762.25 | 1.2 | 1.25 | 155025.26 | 102677.08 | CO-42 | MH-42 | MH-43 | 49.7 | 4547.46 | Circular | 10 | 2.52 | 0.049 | 1.9 | PVC
MH-43 | 762.8 | 759.83 | 1.2 | 2.97 | 154996.75 | 102717.78 | CO-43 | MH-43 | MH-44 | 30.9 | 4590.96 | Circular | 10 | 2.56 | 0.05 | 2.1 | PVC
MH-44 | 760.1 | 758.29 | 1.2 | 1.81 | 154970.29 | 102733.77 | CO-44 | MH-44 | MH-45 | 30.8 | 4633.47 | Circular | 10 | 2.56 | 0.05 | 1.3 | PVC
MH-45 | 758 | 756.75 | 1.2 | 1.25 | 154943.87 | 102749.67 | CO-45 | MH-45 | MH-46 | 49.8 | 4705.92 | Circular | 10 | 2.23 | 0.034 | 1 | PVC
MH-46 | 756.3 | 755.05 | 1.2 | 1.25 | 154897.61 | 102768.16 | CO-46 | MH-46 | MH-47 | 50.1 | 4773.93 | Circular | 10 | 2.37 | 0.039 | 1 | PVC
MH-47 | 754.32 | 753.07 | 1.2 | 1.25 | 154851.02 | 102786.68 | CO-47 | MH-47 | MH-48 | 50 | 4837.03 | Circular | 10 | 2.16 | 0.031 | 1.2 | PVC
MH-48 | 753.21 | 751.53 | 1.2 | 1.68 | 154804.53 | 102805.18 | CO-48 | MH-48 | MH-49 | 49.9 | 4895.24 | Circular | 10 | 2.6 | 0.05 | 1.4 | PVC
MH-49 | 750.6 | 749.04 | 1.2 | 1.56 | 154758.18 | 102823.65 | CO-49 | MH-49 | MH-50 | 33.4 | 4931.38 | Circular | 10 | 2.61 | 0.05 | 1.6 | PVC
MH-50 | 749.6 | 747.37 | 1.2 | 2.23 | 154727.16 | 102835.97 | CO-50 | MH-50 | MH-51 | 34.6 | 4966.65 | Circular | 10 | 2.61 | 0.05 | 1.6 | PVC
MH-51 | 747.1 | 745.64 | 1.2 | 1.46 | 154695.01 | 102848.77 | CO-51 | MH-51 | O-1 | 33.8 | 4997.06 | Circular | 10 | 2.62 | 0.05 | 1.1 | PVC
O-1 | 745.2 | 743.95 | 1.2 | 1.25 | 154665.24 | 102864.89