## Sheet1
Table ( B5 ) Sanitary Sewer Design Report For ( Line Road C)
Manhole Report | [6 empty] | Pipe Report
Label | Ground Elevation (m) | Invert Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | X coordinate (m) | Y coordinate (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (m³/day) | Section Shape | Section Size (in) | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 877.2 | 872.48 | 1.2 | 4.73 | 152424.7 | 101538.88 | CO-1 | MH-1 | MH-2 | 49.9 | 34.79 | Circular | 8 | 0.73 | 0.08 | 4 | PVC
MH-2 | 872.25 | 868.48 | 1.2 | 3.77 | 152461.67 | 101505.33 | CO-2 | MH-2 | MH-3 | 51.1 | 77.19 | Circular | 8 | 0.93 | 0.08 | 3.2 | PVC
MH-3 | 867.54 | 864.48 | 1.2 | 3.06 | 152501.51 | 101473.3 | CO-3 | MH-3 | MH-4 | 31.5 | 110.97 | Circular | 8 | 1.05 | 0.08 | 2.5 | PVC
MH-4 | 864.29 | 861.96 | 1.2 | 2.33 | 152533.02 | 101473.68 | CO-4 | MH-4 | MH-5 | 37.1 | 153.06 | Circular | 8 | 1.15 | 0.08 | 1.7 | PVC
MH-5 | 860.51 | 858.99 | 1.2 | 1.52 | 152570.14 | 101475.06 | CO-5 | MH-5 | MH-6 | 35.4 | 196.58 | Circular | 8 | 1.24 | 0.08 | 1.2 | PVC
MH-6 | 857.36 | 856.16 | 1.2 | 1.2 | 152605.5 | 101475.58 | CO-6 | MH-6 | MH-7 | 35.4 | 228.01 | Circular | 8 | 1.04 | 0.042 | 1 | PVC
MH-7 | 855.88 | 854.68 | 1.2 | 1.2 | 152632.31 | 101498.66 | CO-7 | MH-7 | MH-8 | 31.4 | 257.67 | Circular | 8 | 1 | 0.034 | 1 | PVC
MH-8 | 854.82 | 853.61 | 1.2 | 1.2 | 152655.48 | 101519.79 | CO-8 | MH-8 | MH-9 | 31.6 | 290.19 | Circular | 8 | 0.66 | 0.009 | 1 | PVC
MH-9 | 854.52 | 853.31 | 1.2 | 1.2 | 152678.61 | 101541.33 | CO-9 | MH-9 | MH-10 | 40.1 | 357.52 | Circular | 8 | 1.38 | 0.064 | 1 | PVC
MH-10 | 851.94 | 850.73 | 1.2 | 1.2 | 152715.21 | 101524.96 | CO-10 | MH-10 | MH-11 | 48.5 | 489.36 | Circular | 8 | 1.49 | 0.062 | 1 | PVC
MH-11 | 848.91 | 847.71 | 1.2 | 1.2 | 152758.16 | 101502.41 | CO-11 | MH-11 | MH-12 | 37.4 | 613.03 | Circular | 8 | 1.13 | 0.024 | 1 | PVC
MH-12 | 848.03 | 846.83 | 1.2 | 1.2 | 152794.6 | 101494.39 | CO-12 | MH-12 | MH-13 | 50.9 | 782.08 | Circular | 8 | 1.36 | 0.032 | 1 | PVC
MH-13 | 846.41 | 845.21 | 1.2 | 1.2 | 152843.6 | 101480.72 | CO-13 | MH-13 | MH-14 | 49.9 | 953.32 | Circular | 8 | 1.66 | 0.049 | 1 | PVC
MH-14 | 843.98 | 842.77 | 1.2 | 1.2 | 152890.28 | 101463.07 | CO-14 | MH-14 | MH-15 | 50.2 | 1137.74 | Circular | 8 | 1.8 | 0.053 | 1 | PVC
MH-15 | 841.35 | 840.15 | 1.2 | 1.2 | 152937.03 | 101444.78 | CO-15 | MH-15 | MH-16 | 49.8 | 1355.08 | Circular | 8 | 1.8 | 0.046 | 1 | PVC
MH-16 | 839.07 | 837.86 | 1.2 | 1.2 | 152983.47 | 101426.92 | CO-16 | MH-16 | MH-17 | 50.3 | 1565.79 | Circular | 8 | 1.7 | 0.035 | 1 | PVC
MH-17 | 837.31 | 836.1 | 1.2 | 1.2 | 153028.7 | 101404.96 | CO-17 | MH-17 | MH-18 | 44.8 | 1786.32 | Circular | 8 | 1.63 | 0.028 | 1 | PVC
MH-18 | 836.05 | 834.85 | 1.2 | 1.2 | 153068.4 | 101384.22 | CO-18 | MH-18 | MH-19 | 47.4 | 2017.31 | Circular | 8 | 1.23 | 0.012 | 1 | PVC
MH-19 | 835.47 | 834.26 | 1.2 | 1.2 | 153114.69 | 101374.09 | CO-19 | MH-19 | MH-20 | 49.7 | 2256.82 | Circular | 8 | 1.4 | 0.016 | 1 | PVC
MH-20 | 834.67 | 833.46 | 1.2 | 1.2 | 153163.51 | 101364.84 | CO-20 | MH-20 | MH-21 | 50 | 2488.04 | Circular | 8 | 1.54 | 0.019 | 1 | PVC
MH-21 | 833.7 | 832.5 | 1.2 | 1.2 | 153212.28 | 101354.06 | CO-21 | MH-21 | MH-22 | 50.1 | 2723.52 | Circular | 8 | 1.5 | 0.017 | 1 | PVC
MH-22 | 832.89 | 831.63 | 1.2 | 1.25 | 153260.41 | 101340.28 | CO-22 | MH-22 | MH-23 | 50.4 | 2947.11 | Circular | 10 | 1.22 | 0.009 | 1 | PVC
MH-23 | 832.47 | 831.17 | 1.2 | 1.3 | 153308.81 | 101326.4 | CO-23 | MH-23 | MH-24 | 39.5 | 3146.84 | Circular | 10 | 1.58 | 0.018 | 1 | PVC
MH-24 | 831.72 | 830.46 | 1.2 | 1.25 | 153348.08 | 101322.64 | CO-24 | MH-24 | MH-25 | 38.4 | 3328.26 | Circular | 10 | 1.86 | 0.026 | 1 | PVC
MH-25 | 830.7 | 829.45 | 1.2 | 1.25 | 153385.88 | 101316.1 | CO-25 | MH-25 | MH-26 | 38.3 | 3521.05 | Circular | 10 | 1.84 | 0.025 | 1 | PVC
MH-26 | 829.75 | 828.5 | 1.2 | 1.25 | 153423.3 | 101308 | CO-26 | MH-26 | MH-27 | 50.3 | 3740.42 | Circular | 10 | 1.4 | 0.011 | 1 | PVC
MH-27 | 829.18 | 827.92 | 1.2 | 1.25 | 153472.54 | 101297.51 | CO-27 | MH-27 | MH-28 | 48.9 | 3953.75 | Circular | 10 | 1.3 | 0.009 | 1 | PVC
MH-28 | 828.72 | 827.47 | 1.2 | 1.25 | 153520.33 | 101287.29 | CO-28 | MH-28 | MH-29 | 50.6 | 4183.81 | Circular | 10 | 1.92 | 0.025 | 1 | PVC
MH-29 | 827.5 | 826.24 | 1.2 | 1.25 | 153569.78 | 101276.31 | CO-29 | MH-29 | MH-30 | 49.9 | 4394.91 | Circular | 10 | 2.16 | 0.033 | 1 | PVC
MH-30 | 825.86 | 824.61 | 1.2 | 1.25 | 153618.67 | 101266.27 | CO-30 | MH-30 | MH-31 | 48.1 | 4600.96 | Circular | 10 | 2.1 | 0.029 | 1 | PVC
MH-31 | 824.45 | 823.19 | 1.2 | 1.25 | 153665.69 | 101256.25 | CO-31 | MH-31 | MH-32 | 52 | 4824.65 | Circular | 10 | 2.08 | 0.028 | 1 | PVC
MH-32 | 823.06 | 821.81 | 1.2 | 1.25 | 153716.57 | 101245.4 | CO-32 | MH-32 | MH-33 | 49.8 | 5059.76 | Circular | 10 | 2.04 | 0.025 | 1 | PVC
MH-33 | 821.79 | 820.53 | 1.2 | 1.25 | 153765.3 | 101234.95 | CO-33 | MH-33 | MH-34 | 50 | 5211.86 | Circular | 10 | 2.4 | 0.039 | 1 | PVC
MH-34 | 819.85 | 818.6 | 1.2 | 1.25 | 153814.23 | 101224.56 | CO-34 | MH-34 | MH-35 | 51.5 | 5798.44 | Circular | 10 | 2.44 | 0.038 | 1 | PVC
MH-35 | 817.97 | 816.72 | 1.2 | 1.25 | 153864.63 | 101213.77 | CO-35 | MH-35 | MH-36 | 49.6 | 7032.79 | Circular | 10 | 2.53 | 0.037 | 1 | PVC
Table ( B5.1 ) Sanitary Sewer Design Report For ( Line Road C)
Manhole Report | [6 empty] | Pipe Report
Label | Ground Elevation (m) | Invert Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | X coordinate (m) | Y coordinate (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (m³/day) | Section Shape | Section Size (in) | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-36 | 816.14 | 814.89 | 1.2 | 1.25 | 153883.35 | 101167.8 | CO-36 | MH-36 | MH-37 | 46.6 | 7087.03 | Circular | 10 | 2.26 | 0.028 | 1 | PVC
MH-37 | 814.85 | 813.59 | 1.2 | 1.25 | 153902.09 | 101125.12 | CO-37 | MH-37 | MH-38 | 46.6 | 7184.57 | Circular | 10 | 2.01 | 0.021 | 1 | PVC
MH-38 | 813.88 | 812.62 | 1.2 | 1.25 | 153942.73 | 101102.41 | CO-38 | MH-38 | MH-39 | 49.9 | 7302.47 | Circular | 10 | 1.93 | 0.019 | 1 | PVC
MH-39 | 812.98 | 811.67 | 1.2 | 1.3 | 153986.19 | 101077.81 | CO-39 | MH-39 | MH-40 | 50.1 | 7427.73 | Circular | 10 | 2.54 | 0.036 | 1.1 | PVC
MH-40 | 811.16 | 809.86 | 1.2 | 1.3 | 154029.76 | 101053.02 | CO-40 | MH-40 | MH-41 | 50.1 | 7554.36 | Circular | 10 | 2.71 | 0.042 | 1.1 | PVC
MH-41 | 809.05 | 807.74 | 1.2 | 1.3 | 154073.39 | 101028.4 | CO-41 | MH-41 | MH-42 | 49.8 | 7680.96 | Circular | 10 | 2.23 | 0.026 | 1.1 | PVC
MH-42 | 807.76 | 806.45 | 1.2 | 1.3 | 154116.76 | 101003.84 | CO-42 | MH-42 | MH-43 | 50.1 | 7808.6 | Circular | 12 | 1.81 | 0.014 | 1 | PVC
MH-43 | 807.04 | 805.74 | 1.2 | 1.3 | 154160.35 | 100979.13 | CO-43 | MH-43 | MH-44 | 50.1 | 7937.39 | Circular | 12 | 2.76 | 0.042 | 1 | PVC
MH-44 | 805 | 803.62 | 1.2 | 1.38 | 154203.93 | 100954.4 | CO-44 | MH-44 | MH-45 | 50.1 | 8068.42 | Circular | 15 | 1.24 | 0.005 | 1.4 | PVC
MH-45 | 805.47 | 803.37 | 1.2 | 2.1 | 154247.54 | 100929.71 | CO-45 | MH-45 | MH-46 | 49.9 | 8210.01 | Circular | 15 | 1.24 | 0.005 | 1.4 | PVC
MH-46 | 804.67 | 803.12 | 1.2 | 1.55 | 154291 | 100905.1 | CO-46 | MH-46 | MH-47 | 49.9 | 8347.12 | Circular | 15 | 2.78 | 0.043 | 1.1 | PVC
MH-47 | 802.35 | 800.97 | 1.2 | 1.38 | 154334.37 | 100880.48 | CO-47 | MH-47 | MH-48 | 50.4 | 8489.92 | Circular | 15 | 2.83 | 0.045 | 1 | PVC
MH-48 | 800.11 | 798.73 | 1.2 | 1.38 | 154378.19 | 100855.68 | CO-48 | MH-48 | MH-49 | 50.1 | 8635.24 | Circular | 15 | 1.63 | 0.01 | 1 | PVC
MH-49 | 799.62 | 798.24 | 1.2 | 1.38 | 154421.74 | 100830.93 | CO-49 | MH-49 | MH-50 | 49.8 | 8779.89 | Circular | 15 | 1.26 | 0.005 | 1.1 | PVC
MH-50 | 799.6 | 797.99 | 1.2 | 1.61 | 154464.9 | 100806.18 | CO-50 | MH-50 | MH-51 | 50.6 | 8923.53 | Circular | 15 | 1.26 | 0.005 | 1.4 | PVC
MH-51 | 799.72 | 797.74 | 1.2 | 1.98 | 154506.29 | 100777.11 | CO-51 | MH-51 | MH-52 | 49.8 | 9063.36 | Circular | 15 | 1.7 | 0.011 | 1.3 | PVC
MH-52 | 798.59 | 797.21 | 1.2 | 1.38 | 154547 | 100748.47 | CO-52 | MH-52 | MH-53 | 50.1 | 9202.07 | Circular | 15 | 2.57 | 0.032 | 1 | PVC
MH-53 | 796.98 | 795.6 | 1.2 | 1.38 | 154588.09 | 100719.82 | CO-53 | MH-53 | MH-54 | 49.9 | 9338.15 | Circular | 15 | 2.71 | 0.037 | 1 | PVC
MH-54 | 795.14 | 793.76 | 1.2 | 1.38 | 154628.86 | 100691.13 | CO-54 | MH-54 | MH-55 | 39 | 9442.25 | Circular | 15 | 2.62 | 0.033 | 1 | PVC
MH-55 | 793.85 | 792.47 | 1.2 | 1.38 | 154660.77 | 100668.74 | CO-55 | MH-55 | MH-56 | 38 | 9541.99 | Circular | 15 | 2.98 | 0.047 | 1 | PVC
MH-56 | 792.05 | 790.67 | 1.2 | 1.38 | 154691.98 | 100646.98 | CO-56 | MH-56 | MH-57 | 50.1 | 9649.61 | Circular | 15 | 2.58 | 0.031 | 1 | PVC
MH-57 | 790.48 | 789.1 | 1.2 | 1.38 | 154717.43 | 100603.83 | CO-57 | MH-57 | MH-58 | 50.2 | 9754.7 | Circular | 15 | 2.47 | 0.028 | 1 | PVC
MH-58 | 789.1 | 787.72 | 1.2 | 1.38 | 154742.44 | 100560.25 | CO-58 | MH-58 | MH-59 | 50.2 | 9858.01 | Circular | 15 | 2.16 | 0.019 | 1 | PVC
MH-59 | 788.15 | 786.77 | 1.2 | 1.38 | 154767.52 | 100516.74 | CO-59 | MH-59 | MH-60 | 50.1 | 9959.54 | Circular | 15 | 2.99 | 0.046 | 1 | PVC
MH-60 | 785.85 | 784.47 | 1.2 | 1.38 | 154792.55 | 100473.3 | CO-60 | MH-60 | MH-61 | 50.1 | 10049.66 | Circular | 15 | 2.86 | 0.04 | 1 | PVC
MH-61 | 783.83 | 782.45 | 1.2 | 1.38 | 154817.54 | 100429.89 | CO-62 | MH-61 | O-1 | 51.5 | 10566.17 | Circular | 15 | 2.69 | 0.033 | 1 | PVC
O-1 | 782.18 | 780.8 | 1.2 | 1.38 | 154843.22 | 100385.28