  - Introduction

ETAP offers a suite of fully integrated Electrical Engineering software solutions including arc flash, load flow, short circuit, transient stability, relay coordination, cable ampacity, optimal power flow, and more. Its modular functionality can be customized to fit the needs of any company, from small to large power systems.

ETAP Real-Time is a fully-integrated suite of software applications that provides intelligent power monitoring, energy management, system optimization, advanced automation, and real-time prediction.

ETAP is the most comprehensive enterprise solution for design, simulation, operation, control, optimization, and automation of generation, transmission, distribution, and industrial power systems

ETAP Smart Grid offers comprehensive applications enabling electrical utilities to plan, coordinate, and safely operate their grid. This real-time system has the ability to manage, control, visualize, optimize, and automate power transmission and distribution networks

So we will use EtAP 12.6 program in our project to analysis and improve Adahiriya Network.

  - Modeling the network

The design of the Adahiriya network needs a large amount of data represented as 55 transformer, and the length of the cables and overhead lines. The details of the distribution network are shown in Appendix E1 for balanced loads and unbalanced loads.

Figure (6.1): The distribution network (33/0.4) KV of Adahiriya city.

6.2.1    Cables and overhead lines

Adahiriya network has a large number on cables and overhead with a different manufacturer, which has an impedance value effect on the system, the all data of distribution line analysis in Etap in Appendix E4.

Table 6.1:  Cables and overhead lines data

| Line Type | Resistance (Ω/Km) | Reactance (Ω/Km) | Admittance (Ω-1 /Km) |
| --- | --- | --- | --- |
| Coyote | 0.216 | 0.318 | 0 |
| Dog | 0.269 | 0.326 | 0 |
| Rabbit | 0.529 | 0.347 | 0 |
| Nexans, single core XLPE, 95 mm2 | 0.321 | 0.22 | 5.2*10-5 |

6.3 Etap circuit analysis and result

Redistribution of loads on the electricity network has impact on the operation and performance of the network, and there are some changes to the characteristics of the network such as the voltage drop, losses and the power factor. The output results from the ETAP in Appendix F.

6.3.1    Voltage Validation

First of all, to ensure the result gained from the ETAP program are approximately closed to the real data were collected from the network by power quality analyzer voltage validation should be checked to verify the result and to build accurate rule to analyze the network. In the Figure (6.2) note the real voltage versus the simulation voltage are approximately the same with a small different.

Table 6.4: comparison between the simulation and real voltage

| Transformer | simulation voltage | real voltage | percentage of error |
| --- | --- | --- | --- |
| T 34 | 229.67 | 228.86 | 0.35392816 |
| T 35 | 228.80 | 228.1 | 0.30688294 |
| T 38 | 229.24 | 229.46 | -0.09587727 |
| T 21 | 228.78 | 227.3 | 0.65112186 |
| T 18 | 228.71 | 229.82 | -0.48298668 |
| T 16 | 229.37 | 228.75 | 0.27103825 |
| T 43 | 229.5 | 230.8 | -0.563258232 |
| T 45 | 229.1 | 229.3 | -0.08722197 |

Where

percentage of error =simulation voltage-real voltage real voltage                                             (6.1)

Refers to the Table (6.4) and Figure (6.3) note the extent to which the real values of the voltage are taken by the power quality analyzer match in approximately 99 % with the simulation values of the voltage in ETAP program.

Figure (6.3): The simulation and real voltage

### 6.2 Voltage drop

Voltage drop becomes important when the length of power conductor becomes very long because increasing of its impedance. Voltage drop can also occur when unbalance load. Excessive voltage drop can cause loss of efficiency in operation of light, motors and other load for different applications.

Redistribution of loads change the voltage Drop by changing the direction and magnitude of real and reactive power flows, however providing the reactive power to the network leads to increase the voltage on the network and then the one of advantages of Redistribution of loads to improve the voltage Drop. As shown in the Figure (6.5) After Redistribution of loads to the network this lead to reduce the voltage drop on the resistance then the losses are decreasing on the distribution line.

Figure (6.5): Voltage Drop with and without DG for the average load

The following table shows the results after redistributing in case of maximum loads    to improve the voltage levels.

| P.F after % | P.F old % | Voltage after add capacitor | Voltage before add capacitor | Q(KVAR) | Transformer Number |
| --- | --- | --- | --- | --- | --- |
| 89.7 | 89.7 | 0.417 | 0.417 |  | T1 |
| 93.2 | 89.6 | 0.417 | 0.417 | 25 | T2 |
| 93.0 | 89.8 | 0.418 | 0.418 | 25 | T3 |
| 94.9 | 89.4 | 0.415 | 0.414 | 25 | T4 |
| 89.9 | 89.9 | 0.419 | 0.419 |  | T5 |
| 92.4 | 89.7 | 0.418 | 0.418 | 25 | T6 |
| 93.0 | 89.6 | 0.417 | 0.417 | 25 | T7 |
| 92.3 | 89.7 | 0.418 | 0.418 | 25 | T8 |
| 94.2 | 89.7 | 0.418 | 0.417 | 25 | T9 |
| 89.7 | 89.7 | 0.417 | 0.417 |  | T10 |
| 92.4 | 89.7 | 0.418 | 0.417 | 25 | T11 |
| 92.1 | 89.7 | 0.417 | 0.417 | 25 | T12 |
| 89.7 | 89.7 | 0.416 | 0.416 |  | T13 |
| 93.7 | 88.9 | 0.410 | 0.408 | 40 | T14 |
| 93.2 | 89.8 | 0.417 | 0.416 | 25 | T15 |
| 89.8 | 89.8 | 0.416 | 0.416 |  | T16 |
| 89.8 | 89.8 | 0.416 | 0.416 |  | T17 |
| 90.0 | 90.0 | 0.418 | 0.418 |  | T18 |
| 89.7 | 89.7 | 0.416 | 0.416 |  | T20 |
| 93.8 | 89.8 | 0.417 | 0.416 | 25 | T21 |
| 89.8 | 89.8 | 0.416 | 0.416 |  | T22 |
| 89.9 | 89.9 | 0.417 | 0.417 |  | T23 |
| 89.6 | 89.6 | 0.415 | 0.415 |  | T24 |
| 93.5 | 89.7 | 0.415 | 0.414 | 25 | T25 |
| 89.7 | 89.7 | 0.415 | 0.415 |  | T26 |
| 89.7 | 89.7 | 0.415 | 0.415 |  | T27 |
| 89.6 | 89.6 | 0.415 | 0.415 |  | T31 |
| 89.7 | 89.7 | 0.416 | 0.416 |  | T32 |
| 89.6 | 89.6 | 0.415 | 0.415 |  | T37 |
| 89.7 | 89.7 | 0.416 | 0.416 |  | T38 |
| 91.5 | 89.6 | 0.415 | 0.415 | 25 | T39 |
| 89.7 | 89.7 | 0.416 | 0.416 |  | T40 |
| 92.0 | 89.7 | 0.416 | 0.415 | 25 | T41 |
| 91.4 | 89.6 | 0.415 | 0.415 | 25 | T42 |
| 93.0 | 89.6 | 0.416 | 0.415 | 40 | T43 |
| 89.6 | 89.6 | 0.415 | 0.415 |  | T45 |
| 89.6 | 89.6 | 0.415 | 0.415 |  | T46 |
| 92.3 | 89.7 | 0.416 | 0.415 | 25 | T48 |
| 94.5 | 89.7 | 0.416 | 0.415 | 25 | T49 |
| 92.7 | 89.3 | 0.413 | 0.412 | 40 | T50 |
| 92.4 | 89.7 | 0.416 | 0.416 | 25 | T51 |
| 90.6 | 89.1 | 0.412 | 0.411 | 25 | T52 |
| 91.1 | 89.5 | 0.414 | 0.414 | 25 | T55 |
| 91.2 | 89.5 | 0.415 | 0.414 | 25 | T56 |
| 95.9 | 89.5 | 0.414 | 0.413 | 25 | T58 |
| 94.4 | 89.8 | 0.417 | 0.416 | 25 | T59 |
| 94.5 | 89.7 | 0.416 | 0.415 | 25 | T60 |
| 91.4 | 89.6 | 0.415 | 0.414 | 25 | T61 |
| 95.2 | 89.6 | 0.415 | 0.414 | 40 | T62 |
| 95.1 | 89.6 | 0.415 | 0.414 | 40 | T63 |
| 89.8 | 89.8 | 0.415 | 0.415 |  | T64 |
| 95.1 | 89.4 | 0.413 | 0.412 | 25 | T67 |
| 90.0 | 90.0 | 0.419 | 0.419 |  | T74 |
| 89.9 | 89.9 | 0.419 | 0.419 |  | T75 |
| 89.8 | 89.8 | 0.418 | 0.418 |  | T76 |
| 92.4 | 89.7 | 0.417 | 0.417 | 25 | T77 |
| 93.1 | 89.6 | 0.416 | 0.415 | 25 | T78 |
| 93.2 | 89.6 | 0.416 | 0.416 | 25 | T79 |
| 92.9 | 89.6 | 0.416 | 0.415 | 25 | T80 |
| 92.8 | 89.6 | 0.416 | 0.416 | 25 | T81 |
| 89.9 | 89.9 | 0.419 | 0.419 |  | T82 |
| 89.8 | 89.8 | 0.418 | 0.418 |  | T83 |
| 93.0 | 89.8 | 0.418 | 0.418 | 25 | T84 |
| 89.9 | 89.9 | 0.419 | 0.419 |  | T85 |
| 92.4 | 89.7 | 0.418 | 0.418 | 25 | T86 |
| 94.7 | 89.8 | 0.417 | 0.416 | 40 | T89 |
| 90.0 | 89.9 | 0.419 | 0.419 |  | T90 |
| 92.7 | 89.6 | 0.416 | 0.416 | 40 | T96 |
| 93.3 | 89.7 | 0.416 | 0.415 | 40 | T101 |
| 95.0 | 89.6 | 0.414 | 0.413 | 40 | T102 |
| 94.6 | 89.4 | 0.412 | 0.411 | 25 | T103 |
| 94.4 | 89.0 | 0.409 | 0.407 | 40 | T104 |
| 95.0 | 89.6 | 0.414 | 0.413 | 40 | T105 |
| 93.1 | 89.6 | 0.415 | 0.415 | 25 | T106 |
| 92.0 | 89.7 | 0.416 | 0.416 | 25 | T109 |
| 92.0 | 89.7 | 0.416 | 0.416 | 25 | T110 |
| 93.3 | 89.7 | 0.416 | 0.416 | 40 | T111 |
| 89.9 | 89.9 | 0.418 | 0.418 |  | T112 |