## Slide 1
Palestine Polytechnic University College of Engineering
Redistribution analysis of the load on Low Voltage Distribution Network At Al -Dahriya City
Project team:
Abd Al Rahman Khuffash
Alaa Awawdeh Asma Obedo
Supervisior: Dr. Maher Maghalseh

## Slide 2: Outline
Overview
The objective of project
Adahiriya City Network
Unbalance System
Collecting Data and Analysis
ETAP Software
Economical study
Conclusions and Recommendations

## Slide 3: Overview
The idea of the project is to study the unbalance in the low voltage distribution system at AL-dahriya city. Also, study the effect of unbalance on the system losses, power factor, and reliability.
The data about the distribution network and load profile will be collected and analyzed. Then, analytical program (E-TAP) will be used to identify the solution.

## Slide 4: The object of the Project
    Study and analysis the effect of unbalanced load on the Medium Voltage Network.
    Study the different loads and work statistics required for the development of the network.
    Redistributed the loaded on the medium Voltage Network to be balanced.
    Economic Feasibility Study for both case (balanced &unbalanced) and the evaluate the results.
    Reduce the maintenance and running cost of the network.

## Slide 5: Challenges
The company don’t allow to applay the project practically due to time

## Slide 6
Introduction
Medium voltage network description.
Component of the network
Adahiriya City Network

## Slide 7
Introduction
Adahiriya is a Palestinian city in southwest of the Hebron Governorate far from the city 23 Km.
The population of Adahiriya is about 36000.
The area of Adahiriya is 120854 acres.

## Slide 8
Medium voltage network description
SELCO is a power distribution company works at medium voltage level (33KV)
It takes its energy from the IEC to supply three municipalities Adahiriya, Yatta, and Dura.
The electrical power system of Adahiriya is compact and integrated structure in hierarchical aspect .
It acts as a good role in the distribution of the energy to the consumers.
It satisfies the main factors that ensure the continuity in the power flow to the consumers .

## Slide 9
Component of the network
SELCO has all required component to keep the system operate at security and reliable case.
1. Distribution lines 2. Distribution Transformers
3. Fuses 4. Towers
5. Disconnector switch 6. Surge Arresters
7. Insulators

## Slide 10: Unbalance of the system
Unbalance Definition:
A three-phase power system is called balanced if the three-phase voltages and currents have the same amplitude and are phase shifted by 120° with respect to each other.
If either or both of these conditions are not met, the system is called unbalanced.
Unbalance voltage
Unbalance current

## Slide 11
Unbalance current
The unbalance of current is the mane cause of the unbalance of the voltage in the system.

## Slide 12
Unbalance voltage
The voltage unbalance percentage (VUP) at the terminal of a machine as given by the National Electrical Manufacturer Association Motor and Generator Standard (NEMA MGI) used in most studies is:

## Slide 13
Causes of Unbalance
large single phase load.
Unbalance impedances.
Switching of three phase heavy loads results in current and voltage which cause unbalance in the system.
A three phase equipment such as induction motor with unbalance in its windings. If the reactance of three phases is not same.

## Slide 14
Effects on the distribution Transformer, cables and overhead lines
Unbalanced loading in a transformer will reduce the capacity of the transformer in a distribution system.
Copper losses vary considerably with the load unbalance.
Copper losses
Reduced life of distribution transformers and underground cables due to additional thermal stresses on insulation.

## Slide 15
Effects on consumer load equipment
The effects on induction machines are heating effects which result in a reduction in efficiency and faster thermal ageing and reduced speed and torque.
The effects on rectifiers are additional third harmonic currents, the rectifier circuit increases losses and may damage the rectifier components.
The effects on inverters are additional losses, noise issues and additional third harmonic.

## Slide 16
How can unbalance be mitigated
Redistribute the loads in such a way that the system becomes more balanced this is most basic solution.
Make balance impedances in the power transmission or distribution system by transposed distribution line.

## Slide 17
Benefits of Load balancing
Load balancing improves the performance of each Bus bar and hence the overall system performance.
Load balancing reduces the job time in Maintenance
Maximum utilization of resources
Higher throughput
Higher reliability
Low cost but high gain

## Slide 18
Collecting data and analysis
Power Quality Analyzers
Data collection
Data analysis

## Slide 19
Power Quality Analyzers

## Slide 20
Power Quality Analyzers
Power Quality Analyzers is a device used to analyze the power on lines and transformer.
By using Fluke 435 the standard IEC61000-4-30 2003 Class A, It is used to obtain data in the form of values and curves such as: voltage, current, Frequency, power, energy, and power factor.

## Slide 21
Data collection
Adahiriya contains 55 electrical Transformer.
It takes 24 hour to collect the data for each substation.
The load ratio of transformers varies between (10-100)% of the rated value.

## Slide 22
Data analysis
To build the Adahiriya electrical network in the Etap software this is needs to analysis data collected by power quality analyzer.
The results obtained from the readings that have been measured on Al-muhtasib Transformer.

## Slide 23
Collecting data and analysis
Data analysis
Apperant power

## Slide 24
Collecting data and analysis
Data analysis
power factor

## Slide 25
Collecting data and analysis
Data analysis
Phase Current(A) | L1 | L2 | L3 | N
Minimum Current | 34 | 18 | 51 | 9
Maximum Current | 86 | 74 | 136 | 42
Average= (86A + 74A + 136A)/ 3 = 98.66A
Max current deviation from average = 136A - 98.66A = 37.33A
= 37.83%

## Slide 26
Software (Etap)
Modeling The Network
E-TAP simulation and result
Economical study

## Slide 27: Software (ETAP)
Introduction
The using of Softwares programs in the modeling of electrical systems.
Why E-tap?

## Slide 28
Software (ETAP)
Modeling the network

## Slide 29
E-TAP simulation and result
Software (ETAP)
Voltage Validation
Chart: voltage (v)
simulation voltage | 229.67 | 228.8 | 229.24 | 228.78 | 228.71 | 229.37 | 229.5 | 229.1
real voltage | 228.86 | 228.1 | 229.46 | 227.3 | 229.82 | 228.75 | 230.8 | 229.3

## Slide 30
Redistribution of loads change the voltage Drop by changing the direction and magnitude of real and reactive power flows.
providing the reactive power to the network leads to increase the voltage on the network.
After Redistribution of loads to the network this lead to reduce the voltage drop on the resistance then the losses are decreasing on the distribution line.
One of advantages of Redistribution of loads to improve the voltage profile.
Software (ETAP)
E-TAP simulation and result
Voltage drop

## Slide 31
Software (ETAP)
E-TAP simulation and result
Voltage drop

## Slide 32
Power Factor
Software (ETAP)
E-TAP simulation and result

## Slide 33: Software (ETAP)
E-TAP simulation and result
Losses
Redistributed loads are reducing the losses on transformer caused by the unbalance system on the network.
Total Losses (kw) | Unbalance | Balance
Minimum load | 125.6 | 24
Average load | 213 | 35.7
Maximum load | 440.4 | 54

## Slide 34
E-TAP simulation and result
Software (ETAP)
Losses

## Slide 35: Software (ETAP)
E-TAP simulation and result
Power Factor Improvement in the Average Load
Capacitor banks installed in the network.

## Slide 36: Software (ETAP)
E-TAP simulation and result
The results after adding capacitors in order to improve the P.F after balancing average load.

## Slide 37: Economical study
Another face of the project which is a very important in any project, it's the economic study to the system.
Cost of losses before and after balancing load.

## Slide 38: Economical study
The total Cost of losses of transformers for three phases
Total Cost Losses (NIS/year) | Unbalance | Balance | Saving in losses
Minimum load | 396092 | 75686.4 | 320405
Average load | 671716 | 112583 | 559133
Maximum load | 1388845 | 170294 | 1218551

## Slide 39: Conclusion And Recommendations
Etap software can design the power system precisely as it exists in the real world, and gives the measurement accurately matching the practical system.
Conclusion 1
Conclusion 2
The present study on Al-Dahiriya MV network show that the percentage loadings on the transformers are less than 50%. However, there is no need for replacing the transformers for the coming years.
Conclusion

## Slide 40: Conclusion And Recommendations
Conclusion 3
Conclusion 4
Conclusion
Redistribution the loads at Al-Dahiriya network can reduce the voltage drop, increase the power factor, and reduce the losses.
The analysis at Al-Dahiriya network show that the losses is up to 440kWh due to the unbalance load. This can cost SELCO Company up to 1388845.44 NIS per year. However. The balance loading can be reduced up to 50 kWh, which mean that the losses can be reduced by 88%. Further, the SELCO company can save money up to 1218551.04 NIS per year.

## Slide 41: Conclusion And Recommendations
Recommendations
Recommendation 1
Recommendation 2
Strict procedures to improve the power factor on the industrial loads to reduce the losses in the network
Design a SCADA to supervision on the network, and it's simplicity in collecting the data.

## Slide 42: Conclusion And Recommendations
Recommendations
Recommendation 3
Apply GIS system to find out loads for each customer and on which phase was connected.

## Slide 43
Thank you for attention