4.1 Introduction

A fire fighting system is probably the most important of the building services, as its aim is to protect human life and property, strictly in that order. fire fighting systems and equipment vary depending on the age, size, use and type of building construction.

4.2 Types of fire fighting system

    - Fire extinguishers.

    - Fire hose reels.

    - Fire hydrant systems.

    - Automatic sprinkler systems.

4.2.1 Fire extinguishers

Fire extinguishers are provided for a 'first attack' fire fighting measure generally undertaken by the occupants of the building before the fire service arrives. It is important that occupants are familiar with which extinguisher type to use on which fire.

Most fires start as a small fire and may be extinguished if the correct type and amount of extinguishing agent is applied whilst the fire is small and controllable.

The principle fire extinguisher types currently available include:

Figure 4.1 : Fire extinguishers

4.2.2 Fire hose reel

Fire hose reel systems consist of pumps, pipes, water supply and hose reels located strategically in a building, ensuring proper coverage of water to combat a fire.

The system is manually operated and activated by opening a valve enabling the water to flow into the hose that is typically 30 meters away. The usual working pressure of a firehouse can vary between 8 and 20 (116 and 290 psi).

Fire hose reels are provided for use by occupants as a first attack firefighting measure but may, in some instances, also be used by firefighters. When stowing a fire hose reel, it is important to first attach the nozzle end to the hose reel valve, then close the hose reel valve, then open the nozzle to relieve any pressure in the wound hose, then close the nozzle.

Figure 4.2: Fire hose reel

4.2.3 Fire hydrant  system

Fire hydrant systems are installed in buildings to help fire fighters quickly attack the fire.

Essentially, a hydrant system is a water reticulation system used to transport water in order to limit the amount of hose that fire fighters have to lay; thus speeding up the fire fighting process.

Fire hydrants are for the sole use of trained fire fighters (which includes factory fire fighting teams). Because of the high pressures available serious injury can occur if untrained persons attempt to operate the equipment connected to such installations. Fire hydrant systems sometimes include ancillary parts essential to their effective operation such as pumps, tanks and fire service booster connections. These systems must be maintained and regularly tested if they are to be effective when needed.

Figure 4.3: Fire Hydrant System

4.2.4 Automatic sprinkler system

Time is essential in the control of fire. Automatic sprinkler systems are one of the most reliable methods available for controlling fires. Today's automatic fire sprinkler systems offer state of the art protection of life and property from the effects of fire. Sprinkler heads are now available which are twenty times more sensitive to fire than they were ten years ago.

A sprinkler head is really an automatic (open once only) tap. The sprinkler head is connected to a pressurized water system. When the fire heats up the sprinkler head, it opens at a preset temperature, thus allowing pressurized water to be sprayed both down onto the fire and also up to cool the hot smoky layer and the building structure above the fire. This spray also wets combustible material in the vicinity of the fire, making it difficult to ignite, thereby slowing down or preventing fire spread and growth.

When a sprinkler head operates, the water pressure in the system drops, activating an alarm, which often automatically calls the fire brigade via a telephone connection.

4.3 Select the most effective type :

After the identification of the fire systems now the best performance for the building and offices l is hose reel and  extinguisher.

The number of hose reels to be used in building  is 6 fire hose reels for all floors .

4.4 Pipe size calculation:

The fire hose reel system is to be used, so the pipe size for this system will be calculated as follows:

The minimum flow rate for single cabinet = 23 (l/min). Then :

Table 4.1:Pipe schedule - standpipes and supply piping

Then the table (4.1) is to be used to calculate the pipe size by follow the next procedure. First, the total flow rate is determined which is 575 l/min for our calculation sample. Then the total distance of piping from farthest outlet is to be chosen. Finally, the intersection between the two values in table (4.2) will give the size of pipe supply, which is equal to 4''.

Then to determine the outlet pipe size from pipe supply to hose connection For this building.

The selection diameter is (2 in.) hose stations to supply water for use primarily by the building occupants or by the fire department during initial response.

4.5 Fire fighting  pumps

Continuous water and pumping station supply should always be available and ready to fight fire, the following three pumps should be connected to a suction header (from water tank), and discharge header (to fire fighting network).

Pumping should be included :

    - Electrical fire fighting pump.

    - Diesel Fire fighting Pump,(Stand-by pump). Diesel pump works if:

      - The electrical pump is out of service, or if there is a lack of electricity.

      - The electrical pump is working but can’t satisfy system water requirements.

    - Jockey Pump: work to make up the system pressure in case of leakage or during the first seconds of fire.

Pump that used in building made by PEERLESS PUMP Company. Mode: Peerless-J-J65F.

(See Cataloge).