ABSTRACT

The aim of the project is to design of Mechanical Systems for Headquarters Charities building which is located in Hebron city-Abu Ktaila . This building consists of  Five Floors with Total area of 2000 m2, While these services are certainly designed to verify human comfort.

In this project, chosen the Air Conditioning System type Variable Refrigerant Flow (VRF) with known advantages  efficient and economical . Also, using the technique of Grey Water conventional treatment to be used in irrigation  and flushing valve in order to save water.

Using modern Software Autodesk Revit to built the Mechanical Services like HVAC-VRF, Plumbing and Fire fighting , Estimation the heating and cooling loads of the Space Zones .

المـــلـــخـــص

الهدف من المشروع هو تصميم نظام ميكانيكي لبناء مجمع الجمعيات الخيرية في مدينة الخليل-أبو اكتيلا. يتكون هذا المبنى من خمسة طوابق بمساحة إجمالية 2000 م²، في حين تم تصميم هذه الخدمات لتحقيق الراحة البشرية.

في هذا المشروع، اختيار نظام تكييف الهواء نوع (VRF) مع مزايا معروفة كفاءةً واقتصادية ً، أيضا إستخدام تقنية معالجه تقليدية للمياه الرمادية لاستخدامها في الري و تغذية صمام التواليت من أجل توفير المياه.

استخدام برنامج أوتوديسك ريفيت لإنشاء الخدمات الميكانيكية مثل HVAC -VRF، السمكرة، مكافحة الحرائق ، التقدير للأحمال الحرارية والتبريد للحيز .

| Title |  |  | List of Contents |  |  |  | Page |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Abstract |  |  | ................................................................... |  |  |  | III |  |
| List of Contents |  |  | ................................................................... |  |  |  | IV |  |
| List of Tables |  |  | ................................................................... |  |  |  | VI |  |
| List of Figures |  |  | ................................................................... |  |  |  | VIII |  |
| Chapter One: Introduction |  |  |  |  |  |  |  |  |
| 1.1 | Introduction…………………………………………...... |  |  |  |  |  | 1 |  |
| 1.2 | Project objectives……………………………………..... |  |  |  |  |  | 1 |  |
| 1.3 | Project importance…………………………………....... |  |  |  |  |  | 1 |  |
| 1.4 | Building description…………………………………..... |  |  |  |  |  | 2 |  |
| 1.5 | Project outline ……………………………………......... |  |  |  |  |  | 2 |  |
| 1.6 | Key words……………………….…………………….. |  |  |  |  |  | 2 |  |
| 1.7 | Time planning………………………………………….. |  |  |  |  |  | 3 |  |
| Chapter Two: Heating And Cooling Loads " HVAC System" |  |  |  |  |  |  |  |  |
| 2.1 | Overview……………………………………………...... |  |  |  |  |  | 4 |  |
| 2.2 | Thermal comfort criteria for inside design condition… |  |  |  |  |  | 4 |  |
|  | 2.2.1 | Inside design temperature for unheated spaces |  |  |  |  | 8 |  |
| 2.3 | Overall heat transfer coefficient……………………...… |  |  |  |  |  | 9 |  |
|  | 2.3.1 | Sample calculation for Heating loads for director room1 |  |  |  |  | 10 |  |
|  | 2.3.2 | Sample calculation for Cooling loads for director room1 |  |  |  |  | 15 |  |
| 2.4 | Estimation Summary Heating and Cooling loads…..… |  |  |  |  |  | 22 |  |
| 2.5 | Variable Refrigerant Flow System(VRF)........................ |  |  |  |  |  | 23 |  |
|  | 2.5.1 | Overview of VRF............................................ |  |  |  |  | 23 |  |
|  | 2.5.2 | Variable Refrigerant Flow description............. |  |  |  |  | 23 |  |
|  | 2.5.3 | Design consideration for VRF System.............. |  |  |  |  | 26 |  |
| 2.6 | Advantages of VRF system…………………………...... |  |  |  |  |  | 29 |  |
| 2.7 | Selection Unit…………………………………………... |  |  |  |  |  | 31 |  |
| 2.8 | Mechanical Ventilation……………………………….... |  |  |  |  |  | 34 |  |
| Chapter Three: Plumbing System |  |  |  |  |  |  |  |  |
| 3.1 | Introduction…………………………………………...... |  |  |  |  |  |  | 36 |
| 3.2 | Water supply system…………………………................ |  |  |  |  |  |  | 37 |
|  | 3.2.1 | Overview……………………………………… |  |  |  |  |  | 37 |
|  | 3.2.2 | Calculation of hot and cold water supply systems |  |  |  |  |  | 37 |
|  | 3.2.3 | Pipe size calculations…………………….......... |  |  |  |  |  | 39 |
| 3.3 | Hot water system Recirculation ……………………...... |  |  |  |  |  |  | 43 |
| 3.4 | 3.3.1 | Return pipe diameter calculation..................... |  |  |  |  |  | 43 |
|  | Selection……………………………………..………..... |  |  |  |  |  |  | 46 |
|  | 3.4.1 | selection for cold water pump…….................... |  |  |  |  |  | 46 |
|  | 3.4.2 | selection for cold Water tank .......................... |  |  |  |  |  | 48 |
|  | 3.4.3 | selection for Boiler…………………................ |  |  |  |  |  | 48 |
|  | 3.4.4 | selection for Hot water central tank size…….... |  |  |  |  |  | 50 |
| 3.5 | Sanitary Drainage system…………………………....... |  |  |  |  |  |  | 52 |
|  | 3.5.1 | Definition of Drainage System…………......... |  |  |  |  |  | 52 |
|  | 3.5.2 | Component of Drainage system…………........ |  |  |  |  |  | 52 |
|  | 3.5.3 | Sanitary Drainage…………………………...... |  |  |  |  |  | 53 |
|  |  | 3.5.3.1 |  |  | Design procedure and pipe sizing.. |  |  | 53 |
|  |  | 3.5.3.2 |  |  | Black Water Pipe sizing …............. |  |  | 54 |
|  |  | 3.5.3.3 |  |  | Grey Water Pipe sizing for............. |  |  | 56 |
| 3.6 | Manholes design…………………………...................... |  |  |  |  |  |  | 58 |
|  | 3.6.1 | manhole calculation........................................... |  |  |  |  |  | 58 |
| 3.7 | Storm Drainage……………………………………........ |  |  |  |  |  |  | 60 |
| Chapter Four: Firefighting system |  |  |  |  |  |  |  |  |
| 4.1 | Introduction…………………………...……………....... |  |  |  |  |  | 62 |  |
| 4.2 | Classification of firefighting system………...……......... |  |  |  |  |  | 62 |  |
|  | 4.2.1 | Fire Extinguishers……………………….......... |  |  |  |  | 62 |  |
|  | 4.2.2 | Fire Hose Reel ………………………….......... |  |  |  |  | 63 |  |
|  | 4.2.3 | Fire Hydrant System…………...…………....... |  |  |  |  | 64 |  |
|  | 4.2.4 | Automatic Sprinkler System…………….......... |  |  |  |  | 64 |  |
| 4.3 | The system selection………………………………........ |  |  |  |  |  | 65 |  |
| 4.4 | pipe size calculation ………………………………........ |  |  |  |  |  | 65 |  |
| 4.5 | Fire fighting pumps………………………….................. |  |  |  |  |  | 66 |  |
| REFERENCES |  | ..................................................................... |  |  |  |  | 67 |  |
| APPENDIX A |  | ........................................................................... |  |  |  |  | 69 |  |
| APPENDIX B |  | ........................................................................... |  |  |  |  | 79 |  |
| CATALOUGE |  | ........................................................................... |  |  |  |  | 101 |  |

|  | List of Tables |  |  |
| --- | --- | --- | --- |
| Title |  |  | Page |
| 1.1 | Time table for first semester |  | 3 |
| 1.2 | Time table for next semester |  | 3 |
| 2.1 | The values of inside film resistance of the air film |  | 6 |
| 2.2 | The values of outside film resistance of the air film |  | 7 |
| 2.3 | Inside and outside conditions in Hebron City |  | 7 |
| 2.4 | Overall heat Transfer Coefficient |  | 9 |
| 2.5 | Summary heating and cooling loads |  | 14 |
| 2.6 | Value of CLTD correction by solar effect |  | 16 |
| 2.7 | The value of CLTD correvtion°C by solar transmission |  | 17 |
| 2.8 | External cooling loads conduction due to ∆T |  | 20 |
| 2.9 | Transmitted heat gains |  | 21 |
| 2.10 | Conduction due to (CLTD) |  | 21 |
| 2.11 | Internal cooling loads |  | 21 |
| 2.12 | The value of infiltration |  | 21 |
| 2.13 | The value of ventilation |  | 21 |
| 2.14 | Ventilation for toilets and kitchens |  | 22 |
| 2.15 | Summary heating and cooling loads |  | 22 |
| 2.16 | Outdoor units (Heat Pump) |  | 31 |
| 2.17 | Bill of Quantity of Outdoor and Indoor units for All |  | 32 |
|  | Floors |  |  |
| 2.18 | The Nominal Capacity of Outdoor and Indoor Units |  | 33 |
| 2.19 | Ventilation rate |  | 34 |
| 3.1 | The Fixture Unit load |  | 38 |
| 3.2 | The Load WSFU and Demand (GPM) for all Floors |  | 39 |
| 3.3 | The size of cold water pipes |  | 40 |
| 3.4 | Total calculation of the risers |  | 41 |
| 3.5 | Properties of cold water riser |  | 41 |
| 3.6 | Properties of hot water riser |  | 41 |
| 3.7 | Approximate insulated piping heat loss and surface Temperature |  | 43 |
| 3.8 | Properties of riser( Recirculation) |  | 45 |
| 3.9 | Fixture unit loads (GPH) |  | 50 |
| 3.10 | The hot water demand per fixture for all floors (GPH) |  | 50 |
| 3.11 | Hot water demand per fixture for various types of buildings |  | 51 |
| 3.12 | Sizing stack A of black water |  | 55 |
| 3.13 | Sizing stack B of black water |  | 55 |
| 3.14 | Sizing of black water stacks and building drain. |  | 55 |
| 3.15 | Sizing stack B of Grey water |  | 56 |
| 3.16 | Sizing stack A of Grey water |  | 57 |
| 3.17 | Sizing of Grey stacks and building drain. |  | 57 |
| 3.18 | Diameter of the manhole according to their depth |  | 58 |
| 3.19 | Black water manholes |  | 59 |
| 3.20 | Gray water manholes |  | 60 |
| 3.21 | Storm Water Manholes |  | 61 |
| 4.1 | Pipe schedule - standpipes and supply piping |  | 65 |

|  | List of Figures |  |
| --- | --- | --- |
| Title |  | Page |
| 2.1 | Human comfort chart | 5 |
| 2.2 | The director room 1 dimensions | 9 |
| 2.3 | One sample of sliding window | 13 |
| 2.4 | The director room 1 dimensions | 15 |
| 2.5 | VRF System with multiple indoor evaporator units | 24 |
| 2.6 | A schematic VRF arrangement | 25 |
| 2.7 | Separation and header tubes | 25 |
| 2.8 | Design limits in VRF system | 27 |
| 2.9 | Pipe work schematic | 27 |
| 2.10 | VRV provides a total solution for integrated climate control | 29 |
| 2.11 | Spilt , Cassette S, Mini cassette and 360 cassette of Indoor Units | 31 |
| 3.1 | Plumbing systems types | 36 |
| 3.2 | Sample WSFU | 37 |
| 3.3 | Cold water riser | 40 |
| 3.4 | Hot Water Risers and solar heating system | 42 |
| 3.5 | Hot and cold water system (Recirculation) | 43 |
| 3.6 | Up feed hot water system with heater at bottom of system | 44 |
| 3.7 | Pump data | 46 |
| 3.8 | Pump Characteristic Curves | 47 |
| 3.9 | Drainage system components | 52 |
| 3.10 | Black Water Stacks | 54 |
| 3.11 | Gray Water Stacks | 56 |
| 3.12 | Manholes details | 59 |
| 3.13 | Storm Water Leaders | 61 |
| 4.1 | Figure 4.1 : Fire extinguishers | 62 |
| 4.2 | Figure 4.2: Fire hose reel | 63 |
| 4.3 | Figure 4.3: Fire Hydrant System | 63 |