2.1 Overview

Heating and cooling loads are the measure of energy needed to be added or removed from a space by the Heating Ventilating and Air Conditioning (HVAC) system to provide the desired level of comfort within a space.

The heating and cooling loads calculation is the first step for HVAC design procedure, selecting HVAC equipment and designing the air distribution system to meet the accurate predicted heating and cooling loads begins with an accurate understanding of the heating and cooling loads on a space .

2.2 Thermal Comfort Criteria for Inside Design Condition

The inside design conditions refer to temperature, humidity, air speed and quality of inside air that will induce comfort to occupants of the space at minimum energy consumption . There are several factors that control the selection of the inside design conditions and expenditure of energy to maintain those conditions:

- The outside design conditions.

- The period occupancy of the conditioned space.

- The level of activity of occupants in the conditioned space.

ASHRAE is an abbreviation for the American Society of Heating Refrigerating and Air Conditioning Engineers. Its Standard Thermal Environmental Conditions for Human Occupancy describes the combinations of indoor space conditions and personal factors necessary to provide comfort in the effective way. There are no static rules that indicate the best atmospheric condition for making all the individual comfortable because human comfort is affected by several factors such as health, age, clothing, etc.  Figure 2.1 shows ASHRAE human comfort chart.

Figure (2.1): Human comfort chart

The ASHRAE comfort chart indicates the acceptable zones of selecting the inside operative temperature and the inside relative humidity for winter heating , summer cooling and year-round air conditioning applications .The operative temperature (Toper,) is the uniform temperature of an imaginary black (ideal radiation ) enclosure in which an occupant would exchange the same amount of heat by convection and radiation as that in the actual non-uniform temperature environment . Thus , the operative temperature can be considered as the temperature of uniform environment that will transfer heat at the same value as the actual environment . it is defined as the numerical average value of the inside air temperature( Ti,) and the mean radiant temperature (TMRT), weighted by their respective heat transfer coefficients as follows :

Toper=hc  Ti+ hr  TMRT   hc  + hr  ……...……………………………………………(2.1)

Where  hC  and  hr  are the convection and radiation heat transfer coefficients, respectively .

The operative temperature depends on the mean radiant temperature , which is given by the equation  (2.2) :

T4MRT=T4g+CV-0.5(Tg-Ta)……………………………..…….…………(2.2)

Where :

T MRT=mean radiant temperature,R or K

Tg=globe temperature , R or K

Ta=ambient air temperature , R or K

V=air velocity ,fpm or m/s

C=0.103×109English units

=0.247×109SI units

The operative temperature ( Toper  ) , at air speed of 0.4 m/s or less and mean radiant temperature value less than 50 °C is approximately equal to the average value of inside air temperature (Ti) ,and mean radiant temperature (TMRT) .

New Effective Temperature :

Effective temperature is not an actual temperature in the sense that it can be measured by a thermometer. It is an experimentally determined index of the various combinations of dry-bulb temperature, humidity, radiant conditions, and air movement that induce the same thermal sensation.

Those combinations that induce the same feeling of warmth or cold are called thermo-equivalent conditions.

| Table (2.1): The values of inside film thermal resistances of the air films (Ri) |  |
| --- | --- |
| Element/ construction materials | Ri [m2.°C/W] (summer and winter) |
| Walls | 0.12 |
| Ceilings | 0.1 |
| Floors | 0.15 |

From Palestinian  code  the air velocity in Hebron is 1.4 m/s .

| Table (2.2): the values of the outside film thermal resistances of the air films(Ro) |  |
| --- | --- |
| Element/ construction materials | Ro [m2.°C/W](winter and summer) |
| Walls | 0.06 |
| Ceilings | 0.04 |
| Floors | 0 |

| Table (2.3): inside and outside conditions in Hebron City |  |  |
| --- | --- | --- |
| Property | For Heating (Winter) | For Cooling (Summer) |
| To (°C) | 4 | 30 |
| Ti (°C) | 24.5 | 24.5 |
| Δ Tadj °C [between conditioned and unconditioned space] | 10.25 | 28.2 |
| Φo % | 72 | 57 |
| Φi % | 35 | 40 |
| Air Velocity m/s | 1.4 | 1.4 |
| hi [kJ/kg] | 42 | 45 |
| ho [kJ/kg] | 13 | 68.5 |
| vi [m3/kg] | 0.855 | 0.855 |
| vo [m3/kg] | 0.7875 | 0.88 |

Where:

| hi Inside Enthalpy | ho : Outside Enthalpy |
| --- | --- |
| vi : Inside Specific volume | vo: outside Specific volume |
| Ti : Inside temperature | To : Outside Temperature |
| Φi :Inside Relative Humidity | Φo : outside Relative Humidity |

2.2.1 Inside Design temperature for Unheated spaces :

In many buildings, certain areas such as hallways and attics are unheated ,these spaces receive their heat through partitions , ceilings and floors . the value of the inside temperature of such unheated spaces (Tun) is between the outside temperature  (To) and the inside design temperature (Ti) .The inside air temperature of unheated or uncooled space that is adjacent to a heated or cooled room should be determined in order to calculate the heat looses through the walls ,ceiling or floor separating the two rooms .The followings guidelines and rules are followed to determine the design temperature of such unheated or uncooled spaces:

- Summer cooling with unconditioned space adjacent :

The temperature of the unconditioned space (Tun) ,for this case is obtained according to the following relation :

Tun= Ti+23 To- Ti……………………………………………………(2.3)

Tun(cooling/summer)= 24.5+23 30-24.5 =28.2°C

Where (Ti) is the inside design temperature of the conditioned space , and (To) is the outside air temperature. Thus , the temperature difference (∆T) , across the wall separating the conditioned and the unconditioned spaces is given by :

∆T=23 To- Ti………………………………………………………(2.4)

- Adjacent space having unusual heat sources:

Such as kitchens ,boiler rooms ,etc. For this case , 5°C or 10°C are added to the outside design temperature when the heat gain of the wall is computed .

Tun= TO+5°C…………………………………………….………..(2.5)

=30+5=35°C

- Heating season with adjacent room unheated :

For this case , the temperature difference across the separating wall is taken as one-half the temperature difference between the inside space and the outside air when the heat loss through the wall of the adjacent room is calculated :

∆Tadj=0.5Ti- To………………………………………..………(2.6)

∆Tadj(heating/winter)=0.524.5- 4=10.25°C

- Ground floors directly on the ground :

The ground temperature needed for the calculation of the heat loss through such floors is taken 5 to 10°C above the outside air temperature ,Alternatively ,some arbitrary temperature difference between the inside space and the ground may be assumed .

2.3  Overall heat Transfer Coefficient :

The overall heat transfer coefficient is a measure of the overall ability of a series of conductive and convective barriers to transfer heat .

To calculate the heat gain from walls, ceiling, ground and doors, one need to calculate the value of overall heat transfer coefficient (U) for each one of them.

The values of (U)is depends on the kind of material that content in walls ,ceiling .

…(2.7)

The Unit of Overall Heat Transfer (U) is

| Table (2.4): Overall heat Transfer Coefficient |  |  |  |
| --- | --- | --- | --- |
| Type of construction |  | Thickness [m] | U (W/ m².°C) |
| Ext. Wall |  | 0.35 | 0.86 |
| Inn. Wall |  | 0.14 | 2.64 |
| Un-con. wall |  | 0.30 | 2.36 |
| Ceiling between floor |  | 0.40 | 0.833 |
| Ceiling last floor | With brick | 0.51 | 0.89 |
|  | Without brick | 0.51 | 0.97 |
| Floor |  | 0.37 | 2.14 |
| Window |  | ----- | 3.50 |
| Door Out steel |  | ----- | 5.80 |
| Door Inn. 50 mm wood |  | 0.045 | 2.70 |

2.3.1 Sample Calculation for Heating loads for Director Room 1:

1-Heating loads calculation :

Figure (2.2) :The Director  room 1 dimensions

Calculate the heat loss from the Director  room 1 at the last floor as a sample :

The height of the room = 3 m

The height of the window = 1.5 m

The height of the door= 2 m

Heat loss through ceiling (Qc) :

Because of its construction, the ceiling is divided into two areas which are area A1 and area A2.

The area A1 is equal to:

A1 = 45 Ac     ….………………………...…………………………..(2.8)

= 45(23.41) = 18.73 m2

And the area A2 is equal to:

A2 = 15 Ac     …………………………...…………………………(2.9)

= 15 (22.5) = 4.68 m2

Qc=UC×AC×Ti-To ………...….……….………….………(2.10)

=(U1A1 +U2A2)×( Ti  - To)

Qc  = (0.89 ×18.73  + 0.97 ×4.68)( 24.5  - 4)

Qc = 428.22 W.

Heat loss through walls (Qw) :

The external wall area is :

Aw,ex = [(5.33×3.0)+(5.0×3.0)]-[1.5(0.8+1.2+1.5)] =25.74 m2

Qw,ex = (Uw,ex× Aw,ex)×( Ti  - To)

= (0.86× 25.74 ) (24.5-4) =453.79 W

There are one space beside the director room1 is unconditioned, so heat loss from unconditioned walls :

The unconditioned temperature is calculate by equation (2.6) :

Tun. = 0.5 (Ti  - To)

= 0.5 (24.5  - 4) = 10.25 °C

The unconditioned area is :

Aw,un. =(3.82× 3.0) =11.46m2

Qw,un. = (( Uun.= Uin) ×Aw,un.)( Ti  - Tun. ) =  (2.64×11.46)(24.5-10.25)

= 431.12 W

Now, the total heat loss from walls is :

Qw,tot  = Qw,ex +Qw,un.   = 453.97 + 431.12  =  885 W

Heat loss through windows (Qg):

there are three windows at the two external wall

Awind.=1.5(1.5+1.2+0.8)=5.25m²

Qg = Ug Ag (Ti  - To)

=(3.5)( 5.25) (24.5-4)   = 376.69 W

Heat loss through internal door (Qd) :

Qd = Ud Ad (Ti  - Ti.)    =(2.7)(2×.9 )(24.5-24.5)

= 0.0 W with the same temperature

Heat loss through floor(Qf) :

Qf = Uf× Af (Tadj  - Ti.)

=(2.14) ×(23.41) ×(29 - 24.5) = 225.44 W

Heat loss through infiltration (Qinf) :

The total heat load due to infiltration is given by the equation

Qinf.,g = Vfvo (hi - ho) ………………………………………………………(2.10)   		= ρo Vf (hi - ho)  , while ρo = 1/vo

Where:

hi: Inside enthalpy of infiltrated air in(kJ/kg)

ho: Outside enthalpy of infiltrated air in (kJ/kg)

Vf: The volumetric flow rate of infiltrated air in (m3/s)

vo ∶ Specific volume in(m3/kg)

Vf = K × L  [0.613 (S1× S2× VO)2 ] 2/3

Where :

K = the infiltration air coefficient.

L: the crack length in meter.

S1: factor that depends on the topography of the location of the building

S2: coefficient that depends on the height of the building.

VO: measured wind speed (m/s)

The value of K, S1 and S2 is obtained from Appendix A of Tables (2.6), (2.7) and (2.8) respectively. K =0.43 , S1 =1  , S2 =0.79  , VO= 1.4 (m/s) from Palestinian code .

Figure (2.3): One sample of  Sliding window

The window is sliding as shown in Figure (2.3) ,then L for three windows with different dimension:
L = [ (2×1. 5) + (3×1.5)]+ [ (2×1. 2) + (3×1.5)]+ [ (2×0.8) + (3×1.5)]  = 20.5 m

Therefore ; 
Vf = (0.43) (20.5) [0.613( 1.0 × 0.79 × 1.4)2  ] 2/3

= 7.2756 m3/h = 2.021× 10-3  m3/s

From the psychometric figure (2.1) human comfort chart can obtain the following moist air properties that correspond to the given inside and outside design conditions : 
vo = 0.79 m3/kg  , hi = 42 kJ/kg  , ho = 13kJ/kg

ρo  = 1/ vo = 1.27 kg / m3

The total heat loss due to infiltration is calculated by equation (2.10) as follows:

Through window :

Qinf.,g = ρo Vf (hi - ho)

= (1.27)( 2.021× 10-3 )( 42 – 13)  = 0.0744kW= 74.43 W

Qinf.,tot =Qinf.,g  = 74.43 W

The total heat loss from the director room 1 is

Qtot = Qw,tot +Qc + Qg +Qd + Qinf.

= 885 + 428.22+225.44+ 376.69  + 74.43

=1989.78 W

Take the safety factor of 10 % for each space of the residence to cover the miscellaneous and emergency heating loads then :

Qtot = 1989.78× 1.1 = 2188.76 [W]=2.19 [kW]

Sample Room( 1):

Inside Design Condition :        Ti = 24.5C ,  φi = 35%

Outside Design Condition :     To = 4 C  ,    φo = 72%

| Table (2.5) Summary of heating loads calculations: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Area (m2) | U (W/m2.°C) | (Ti – To) °C |  | QLoss (W) |
| Walls |  |  |  |  |  |
| Wallin , un con. | 11.46 | 2.64 | (24.5-10.25) =14.25 | 432.12 |  |
| Wall out | 25.74 | 0.86 | (24.5-4) = 20.5 | 453.79 |  |
| Ceiling | Aceiling=23.41 (m²) | U1=0.89 | (24.5-4) = 20.5 | 428.22 |  |
|  | A1=18.7m² | U2=0.97 |  |  |  |
|  | A2=4.68m² |  |  |  |  |
| Floor | 23.41 | 2.14 | (29-24.5) = 4.5 | 225.44 |  |
| Windows | 5.25 | 3.5 | (24-4) = 20 | 376.69 |  |
| Doors |  |  |  |  |  |
| Door in | 1.8 | 2.7 | (24.5-24.5) =0 | ــــــ |  |
| Infiltration |  |  |  |  |  |
| Infiltration Windows | ــــــ | ــــــ | ــــــ | 74.43 |  |
| Infiltration Doors | ــــــ | ــــــ | ــــــ | ــــــ |  |
|  |  |  | Q Loss (W) | 1989.78 |  |
|  | Q[W]loss * Safety Factor (10%) | 2188.76 | Q loss [kW] | 2.19 |  |

2.3.2  Sample Calculation for Cooling loads for Director Room 1:

Figure (2.4) :The Director  room 1 dimensions

CLTD Values :

(CLTD) corr.= (CLTD + LM) k + (25.5 - Tin) + (To,m - 29.4) f…….…….(2.11)

Where:

CLTD: cooling load temperature difference, ˚C

LM: latitude correction factor.

k: color adjustment factor.

Tin: inside comfort design temperature, ˚C

f: attic or roof fan factor.

To,m: outdoor mean temperature,°C

F=1  there is no attic or roof fan

K=1 for dark color walls

The values of   LM (latitude correction factor) is obtained from (Appendix A) Table (2.10) .

For Hebron city: Latitude: 31°31′45″ N

Solar time = 12 hours in summer (from Palestinian code)

Then the CLTD sunlit roof =13 °

DR = Tave,max-Tave,min  = (29.1-17.7)=11.4 °C

To,m=  To- DR2  = To-5.7 =  30 - 5.7 = 24.3 °C

Where

To,m is the outdoor mean temperature.

DR : the daily range temperature which equals to the difference between the average maximum and average minimum daily temperatures for the warmest month of the summer season .

Tave.max. = 29.1 °C , Tave. min.  = 17.7  °C   from Palestinian code in July

Where:  Tave,max  and  Tave,min   is the average maximum and average minimum daily temperatures for the warmest month of the summer season .

| Table (2.6):Value of CLTD corr. for the sunlit roof by solar effect : |  |  |  |
| --- | --- | --- | --- |
| Type | LM | CLTD (°C) | CLTDcorr ( °C) |
| Horizontal Roofs | 0.5 | 13 | 9.4 |
| North wall | 0.5 | 5 | 1.4 |
| South wall | -1.6 | 6 | 0.3 |
| East wall | 0 | 10 | 5.9 |
| West wall | 0 | 8 | 3.9 |
| NE | 0.5 | 8 | 4.4 |
| NW | 0.5 | 7 | 3.4 |
| SE | -0.5 | 9 | 4.4 |
| SW | -0.5 | 8 | 4.5 |
| NNE, NNW | 0.5 | _ | _ |
| ENE , WNW | 0 | _ | _ |
| ESE , WSW | -0.5 | _ | _ |
| SSE , SSW | -1.6 | _ | _ |

For 12 hr solar time  of the external walls we get the CLTD  values  .

CLTD corr.  for the sunlit roof :

(CLTD) corr. sunlit roof = (CLTD + LM) k + (25.5 - Tin) + (To,m - 29.4) f

= (13+0.5) ×1  +     (25.5-24.5)  + (24.3-29.4) ×1

=  9.4 °C

| Table (2.7) the value of CLTD corr. (°C) by Solar Transmission: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Glass windows direction | LM | CLF | SHG W/m2 | SC | CLTD (°C) | CLTD corr. (°C) |
| N | 0.5 | 0.7 | 126 | 0.82 | 5 | 1.4 |
| E | 0 | 0.39 | 678 | 0.82 | 5 | 0.9 |
| S | -1.6 | 0.52 | 227 | 0.82 | 5 | 0.3 |
| W | 0 | 0.14 | 678 | 0.82 | 5 | 0.9 |
| NE | 0.5 | 0.33 | 527 | 0.82 | 5 | 1.4 |
| SE | -0.5 | 0.51 | 473 | 0.82 | 5 | 0.4 |
| SW | -0.5 | 0.23 | 473 | 0.82 | 5 | 0.4 |
| NW | 0.5 | 0.17 | 527 | 0.82 | 5 | 1.4 |

Where CLF is the cooling load factor for glass windows (medium construction) without interior shading from table (2.15) .

LM: from table (2.10), SHG: from table (2.12), CLTD : from table (2.11) .

Cooling Loads :

- Infiltration :

Using Crackage method  :

Qinf.,g = Vfvo (ho – hi)...................................................................................  (2.15)

Where:

hi: Inside enthalpy of infiltrated air in(kJ/kg)

ho: Outside enthalpy of infiltrated air in (kJ/kg)

Vf: The volumetric flow rate of infiltrated air in (m3/s)

Vf = K × L  [0.613 (S1× S2× VO)2 ] 2/3  ................................................... (2.16)

Where:

K = the infiltration air coefficient.

L: the crack length in meter.

S1: factor that depends on the topography of the location of the building

S2: coefficient that depends on the height of the building.

VO: measured wind speed (m/s)

The value of k, S1 and S2 is obtained from Appendix A ,Tables (2.6), (2.7) and (2.8) respectively. K =0.43 , S1 =1.0 , S2 =0.79 , VO= 1.4 (m/s)    from Palestinian code .

And  the window is sliding:
L = [ (2×1. 5) + (3×1.5)]+ [ (2×1. 2) + (3×1.5)]+ [ (2×0.8) + (3×1.5)] = 20.5 m

Therefore ;

Vf  = K × L [0.613 (S1× S2× VO)2 ] 2/3                                                                                                                             
Vf = (0.43) (20.5) [0.613( 1 × 0.79 × 1.4)2  ] 2/3 =7.2756 m3/h = 2.021×10-3 [m3/s]

Qnf.,g = Vf vo (ho – hi)  = (2.021*10-3)/0.88 (68.5 – 45) = 0.0539 [kW] = 53.94W.

- Ventilation:

From Table (2.20) the minimum outside air requirements for mechanical ventilation for the areas of office space =10 L/s/p .

V̍v = 10 * 3 person = 30 L/s = 0.030 m3/s

mv = V̍vV̍o  = 0.0300.88   = 0.034 Kg/s .

Q˙ vn. = m ×Cp air × (Tout -Tin)  = 0.034*1.005*(30-24.5) =0.1879 [kW] =187.93W.

Now for the South West inner wall:

There is a part of this wall near to conditioned space at the same temperature( secretary room1) ,so

Q̓ = U*A*ΔT  = 0.0 W

And there is another wall unconditioned space so :

Auncon.,wall= (3.82 × 3.0) = 11.46 m2

Q̓un con.,wall SE= Uuncon.,wall× A× (ΔTadj,cooling )=  2.64 ×  (11.46) × 28.2 = 853.17 W

Q̓  from the north wall(secretary room1)= Uinn,wall*A*(ΔTadj,cooling ) = 2.64*(11.76)*0.0=    0.0 W (Because there is another conditioned space at the same temperature ) .

For the South West wall:

A SW,window = [(0.8×1.5)]= 1.2 m2

A SW wall = (5.33×3.0) = 15.99 m2

Q̓ SW, wall  = Uouter wall×A×CLTDcorr = 0.86×15.99×4.5 = 61.88 W

A NW,window = [(1.2×1.5)+(1.5×1.5) = 4.05 m2

A NW, wall = (5.0×3.0 )= 15m2

Q̓ NW, wall  = Uouter wall×A×CLTDcorr = 0.86×15.0×3.4 = 43.86 W

Q̓ SW window  =  Q̓solar effect + Q̓solar transmission

Q̓solar effect, SW = Uwindow×Aw×CLTDcorr, sw = 3.5×1.2×0.4 = 1.7 W

Q̓solar transmission, SW= A×SHG×SC×CLF = 1.2×473×0.82×0.51 = 237.37 W

Q̓SW, window  =  1.7+ 237.37= 239 W

For the NW wall :

A NW,window = 4.05 m2

ANW,wall =15 m2

Q̓ wall ,NW = Uouter wall×A×CLTDcorr = 0.86×15×3.4 = 43.86 W

Q̓solar effect, NW = Uwindow×Aw×CLTDcorr,w = 3.5×4.05×1.4= 19.85 W

Q̓solar transmission, NW = A×SHG×SC×CLF = 4.05×527×0.82×0.17 = 297.5 W

Q̓NW, window  =  19.85+297.5 = 317 W

For ground and ceiling :

Q̓ground  = Ug×A× (Tg-Ti) = 2.14×23.41× (26-24.5) = 75 W

U1,C= 0.89 [W/m².°C]

A1,C=45  ×23.41= 18.73 m2

U2,C= 0.97 [W/m².°C]

A2,C=15  ×23.41= 4.7 m2

Q̓ceiling = (U1c×A1 + U2c×A2) ×CLTDcorr,roof  = [( 0.89×18.73) + (0.97×4.7) ×9.4 =199.5W

Heat gain due to lights :

Plight/m2= 30 W/m2

CLFLT = 0.82 FOR 10 hours of operation from table (2.17) Appendix A .

Q̓Lt = Pm2 *A*CLFLT = 30*23.41*0.82 = 575.88 W

Heat gain due to occupants :

Total heat gain = 145 W/person

Sensible heat gain = 87 W/person

CLFoc = 0.85 for 10 hours in space  from table (2.18)  .

Q̓oc.sensible = No.of persons * P senperson*CLFoc = 3*87*0.85 = 221.85 [W]

Q̓oc.latent  = No.of persons * P latperson = 3*(145-87) = 174 [W]

Q̓oc., tot = 221.85 + 174 = 395.85 W

| Table (2.8) External Cooling Loads : Conduction due to (ΔT): |  |  |  |  |
| --- | --- | --- | --- | --- |
| Surface | Area [m2] | U [W/m2. °C] | ΔT [°C] | Q̓ [W] |
| South West Wall | 15.99 | 0.89 | 5.5 | 78.3 |
| North West Wall | 15 | 0.89 | 5.5 | 73.4 |
| Roof Ceiling | 23.41 | U1=0.89,U2=0.97 | 5.5 | 75 |
| SE uncond. wall | 11.46 | 2.64 | 3.7 | 853.2 |
|  |  |  | Total | 1079.9 |

- Transmitted heat gains :

| Table (2.9) : Transmitted heat gains: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Surface | Area (m2) | SHG (W/m2) | SC | CLF | Q̓ (W) |
| SW Glass | 1.2 | 473 | 0.82 | 0.23 | 237.37 |
| NW Glass | 4.05 | 527 | 0.82 | 0.17 | 297.5 |
|  |  |  |  | Total | 534.87 |

ii) Conduction due to CLTD :

| Table (2.10) Conduction due to (CLTD): |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Surface | Area (m2) | CLTD (°C) | LM | CLTDcorr (°C) | Q̓ (W) |
| SW wall | 15.99 | 8 | -0.5 | 3.4 | 61.9 |
| SW Glass window | 1.2 | 5 | -0.5 | 0.4 | 1.7 |
| NW wall | 15 | 7 | 0.5 | 3.4 | 43.86 |
| NW Glass Window | 4.05 | 5 | 0.5 | 1.4 | 19.85 |
| Ceiling | 23.41 | 13 | 0.5 | 9.4 | 199.5 |
|  |  |  |  | Total | 326.81 |

2) Internal Cooling loads :

| Table (2.11) Internal Cooling Loads: |  |  |
| --- | --- | --- |
| Item |  | Q̓ (W) |
| Lights |  | 575.88 |
| Occupants |  | 395.85 |
|  | Total | 971.73 |

3) Infiltration:

| Table (2.12): The value of Infiltration : |  |  |
| --- | --- | --- |
| item |  | Q̓ (W) |
| Infiltration |  | 53.94 |
|  | Total | 53.94 |

4) ventilation :

| Table (2.13) : The value of Ventilation: |  |  |
| --- | --- | --- |
| item |  | Q̓ (W) |
| Ventilation |  | 187.93 |
|  | Total | 187.93 |

Multiply the final result with Factor Of Safety for this room (F.O.S) 10%

QTotal room = ∑Q × F.O.S

=[ 1079.9+534.87+326.81+971.73+53.94+187.93]×1.1

= 3155.2×1.1 = 3470.7 W

= 3.5 kW = 1 Ton Refrigerant

Ventilation Load Summary for Toilet and kitchen is listed in the following table:

| Table (2.14) : Ventilation for twenty four Toilets and eight Kitchens : |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Unit Type | Area ( m2) | Q̓ vent. (kW) | Q̓ vent (kW) with 1.1 F.O.S | Number Of Unit | Total Of Q̓ Vent. (kW) |
| Kitchen | 7.63 | 0.075 | 0.083 | 8 | 0.664 |
| Toilet | 17 | 0.188 | 0.207 | 24 | 4.968 |
|  |  |  | SUM Total |  | 5.632 |

The Total ventilation loads = 5.6 [kW]

2.4  Estimation Of Heating and Cooling loads :

Heating and Cooling Loads for each Floors is listed in the following table:

| Table (2.15):Summary heating and cooling loads: |  |  |  |
| --- | --- | --- | --- |
| Floors | Area ( m2) | Q̓ heating [kW]with Safety Factor | Q̓ cooling [kW] with Safety Factor |
| First | 282 | 67.86 | 54.17 |
| Second | 278 | 66.86 | 53.39 |
| Third | 278 | 66.86 | 53.39 |
| Fourth | 278 | 71.1 | 57.65 |
| Total | 1116 | 272.68 | 218.6 |

2.5  Variable Refrigerant Flow System

2.5.1 Overview

The primary function of all air-conditioning systems is to provide thermal comfort for building occupants. There are a wide range of air conditioning systems available, starting from the basic window-fitted units to the small split systems, to the medium scale package units, to the large chilled water systems, and currently to the variable refrigerant flow (VRF) systems.

Variable refrigerant flow (VRF) is an air conditioning system configuration where there is one outdoor condensing unit and multiple indoor units. The term variable refrigerant flow refers to the ability of the system to control the amount of refrigerant flowing to the multiple evaporators (indoor units), enabling the use of many evaporators of differing capacities and configurations connected to a single condensing unit. The arrangement provides an individualized comfort control, and simultaneous heating and cooling in different zones.

Currently widely applied in large buildings especially in Japan and Europe, these systems are just starting to be introduced in the U.S. The VRF technology/system was developed and designed by Daikin Industries, Japan who named and protected the term variable refrigerant volume (VRV) system so other manufacturers use the term VRF "variable refrigerant flow". In essence both are same.

2.5.2 Variable Refrigerant Flow description

VRF systems are similar to the multi-split systems which connect one outdoor section to several evaporators. VRF systems continually adjust the flow of refrigerant to each indoor evaporator. The control is achieved by continually varying the flow of refrigerant through a pulse modulating valve (PMV) whose opening is determined by the microprocessor receiving information from the thermostat sensors in each indoor unit. The indoor units are linked by a control wire to the outdoor unit which responds to the demand from the indoor units by varying its compressor speed to match the total cooling and/or heating requirements.

VRF systems promise a more energy-efficient strategy (estimates range from 11% to 17% less energy compared to conventional units) at a some what higher cost.

Figure (2.5) : VRF System with multiple indoor evaporator units

The modern VRF technology uses an inverter-driven scroll compressor and permits as many as 48 or more indoor units to operate from one outdoor unit (varies from manufacturer to manufacturer). The inverter scroll compressors are capable of changing the speed to follow the variations in the total cooling/heating load as determined by the suction gas pressure measured on the condensing unit. The capacity control range can be as low as 6% to 100%.

Refrigerant piping runs of more than 200 ft are possible, and outdoor units are available in sizes up to 286,600 Btu/ h = (84 kW).

A schematic VRF arrangement is indicated below:

Figure (2.6) : A schematic VRF arrangement

VRF systems are engineered systems and use complex refrigerant and oil control circuitry. The refrigerant pipe-work uses a number of separation tubes and/or headers (refer schematic figure above).

A separation tube has 2 branches whereas a header has more than 2 branches. Either of the separation tube or header, or both, can be used for branches. However, the separation tube is never provided after the header because of balancing issues.

Figure (2.7) : Separation and header tubes

2.5.3 Design considerations for VRF system

Deciding what HVAC system best suits your application will depend on several variables such as building characteristics, cooling and heating load requirements, peak occurrence, simultaneous heating and cooling requirements, fresh air needs, accessibility requirements, minimum and maximum outdoor temperatures, sustainability, and acoustic characteristics.

Building Characteristics :

VRF systems are typically distributed  systems – the outdoor unit is kept at a far off location like the top of the building or remotely at grade level and all the evaporator units are installed at various locations inside the building. Typically the refrigerant pipe-work (liquid and suction lines) is very long, running in several hundreds of feet in length for large multi-story buildings. Obviously, the long pipe lengths will introduce pressure losses in the suction line and, unless the correct diameter of pipe is selected, the indoor units will be starved of refrigerant resulting in insufficient cooling to the end user. So it is very important to make sure that the pipe sizing is done properly, both for the main header pipe as well as the feeder pipes that feed each indoor unit. The maximum allowable length varies among different manufacturers; however the general guidelines are as follows:

- The maximum allowable vertical distance between an outdoor unit and its farthest indoor unit is 164 ft.

- The maximum permissible vertical distance between two individual indoor units     is 49 ft.

- The maximum overall refrigerant piping lengths between outdoor and the farthest indoor unit is up to 541 ft.

Note: The longer the lengths of refrigerant pipes, the more expensive the initial and operating costs.

Figure (2.8) : Design limits in VRF system

Sustainability

One attractive feature of the VRF system is its higher efficiency compared to conventional units. Cooling power in a VRF system is regulated by means of adjusting the rotation speed of the compressor which can generate an energy saving around 30%.

A VRF system permits easy future expansion when the conditions demand. Over sizing however, should be avoided unless a future expansion is planned.

Figure (2.9) : Pipe work schematic

Other sustainability factors include:

- Use of non-ozone depleting environment-friendly refrigerants such as R 410a .

- Opting for heat pump instead of electrical resistance heating in areas demanding both  cooling and heating .

Heat pumps offer higher energy efficiency.

Simultaneous Heating and Cooling

Some manufacturers offer a VRF system with heat recovery feature which is capable of providing simultaneous heating and cooling. The cost of a VRF-HR is higher than that of a normal VRF heat pump unit and therefore its application should be carefully evaluated.

More economical design can sometimes be achieved by combining zones with similar heating or cooling requirements together. For example, the areas that may require simultaneous heating and cooling are the parametric and interior zones. Parametric areas with lot of glazing and exposure especially towards west and south will have high load variations. A VRF heat pump type system is capable of providing simultaneous heating and cooling exceeding 6 tons cooling requirement.

Using VRF heat pump units for heating and cooling can increase building energy efficiency. The designer must evaluate the heat output for the units at the outdoor design temperature. Supplemental heating with electric resistors shall be considered only when the heating capacity of the VRF units is below the heating capacity required by the application. Even though supplemental heating is considered, the sequence of operation and commissioning must specify and prevent premature activation of supplemental heating.

First Costs

The installed cost of a VRF system is highly variable, project dependent, and difficult to pin down. Studies indicate that the total installed cost of a VRF system is estimated to be 5% to 20% higher than air or water cooled chilled water system, water source heat pump, or rooftop DX system providing equivalent capacity. This is mainly due to long refrigerant piping and multiple indoor evaporator exchanges with associated controls. Building owners often have no incentive to accept higher first costs, even if the claimed payback period is short, as the energy savings claims are highly unpredictable.

2.6  Advantages of VRF system :

Figure (2.10) : VRV provides a total solution for integrated climate control

VRF systems have several key benefits, including:

- Installation Advantages.

VRF systems are lightweight and modular. Each module can be transported easily and fits into a standard elevator.

- Design Flexibility.

A single condensing unit can be connected to many indoor units of varying capacity (e.g., 0.5 to 4 tons [1.75 to 14 kW]) and configurations (e.g., ceiling recessed, wall mounted, floor console). Current products enable up to 20 indoor units to be supplied by a single condensing unit. Modularity also makes it easy to adapt the HVAC system to expansion or reconfiguration of the space, which may require additional capacity or different terminal units.

- Maintenance and Commissioning.

VRF systems with their standardized configurations and sophisticated electronic controls are aiming toward near plug-and-play commissioning.

- Comfort.

Many zones are possible, each with individual set point control. Because VRF systems use variable speed compressors with wide capacity modulation capabilities, they can maintain precise temperature control, generally within ±1°F (±0.6°C), according to manufacturers’ literature.

- Energy Efficiency.

The energy efficiency of VRF systems derives from several factors. The VRF essentially eliminates duct losses, which are often estimated to be between (10-20) percent of total airflow in a ducted system. VRF systems typically include two to three compressors, one of which is variable speed, in each condensing unit, enabling wide capacity modulation. This approach yields high part-load efficiency, which translates into high seasonal energy efficiency, because HVAC systems typically spend most of their operating hours in the range of 40% to 80% of maximum capacity.

- Refrigerant piping

Runs of more than 200 feet (60.96 m) are possible and outdoor units are available in sizes up to 268,000 Btu/ h (84 kW).

2.7  Selection units

This section talks about selection of outdoor and indoor units of VRF system, depending on the “Samsung VRF catalogue”, since this company product is existing in Hebron.

Outdoor and indoor units are selected according to the thermal load of the building.

Outdoor unit

It was chosen three outdoor units with capacity of individual is 60.508 TR DVM S (New)HP Compact (Module) , Cooling capacity = 212.8 kW , Heating capacity = 239.4 kW .

| Table (2.16): Outdoor units (Heat Pump) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Outdoor Unit Name | Dimension (Mm) | Capacity HP | Cooling [kW] | Heating [kW] | No. |
| AM300KXVAGH/TK | 1295*1795*765 | 30 | 84 | 94.5 | 1 |
| AM240KXVAGH/TK | 1295*1795*765 | 24 | 67.2 | 75.6 | 1 |
| AM220KXVAGH/TK | 1295*1795*765 | 22 | 61.6 | 69.3 | 1 |
|  | Total | 76 | 212.8 | 239.4 | 3 |

Indoor unit

In this project there are three types of indoor units selected, which are split , cassette and mini cassette units. The split unit is used for bedrooms, and the cassette units are used for reception and restaurant , and mini cassette units are used for passages and breakfast hall .

The figure below shows the three types of selected units:

Figure (2.11) : Spilt , Cassette S, Mini cassette and 360 cassette of Indoor Units

The selected Outdoor and Indoor units for the building are listed in the tables below:

Table ( 2.17): Bill of Quantity of Outdoor and Indoor units for All Floors :

| Outdoor |  |  |  | Unit |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fl | Name | Model name | Quantity | Fl | Name | Model name | Quan. |
| Roof | Outdoor | AM220KXVAGH/TK | 1 | 4F | 3RD-ROOM-01 | AM090KN4DEH/TK | 3 |
|  |  |  |  | 4F | 3RD-ROOM-02 | AM045KN4DEH/TK | 1 |
|  |  |  |  | 4F | 3RD-ROOM-04 | AM045FNNDEH/TK | 2 |
|  |  |  |  | 4F | 3RD-ROOM-05 | AM036FNNDEH/TK | 1 |
|  |  |  |  | 4F | 3RD-ROOM-07 | AM028FNNDEH/TK | 2 |
|  |  |  |  | 4F | 3RD-ROOM-06 | AM022FNTDEH/TK | 1 |
|  |  |  |  | 4F | 3RD-ROOM-08 | AM045FN4DEH/TK | 1 |
|  |  |  |  | 3F | 2ND-ROOM-01_1 | AM071KN4DEH/TK | 4 |
|  |  |  |  | 3F | 2ND-ROOM-02 | AM022FNQDEH/TK | 2 |
|  |  | AM240KXVAGH/TK | 1 | 3F | 2ND-ROOM-03 | AM056FNNDEH/TK | 1 |
|  |  |  |  | 3F | 2ND-ROOM-04 | AM036FNNDEH/TK | 3 |
|  |  |  |  | 3F | 2ND-ROOM-06 | AM112FNMDEH/TK | 1 |
|  |  |  |  | 3F | 2ND-ROOM-12 | AM045FNNDEH/TK | 1 |
|  |  |  |  | 3F | 2ND-ROOM-14 | AM090FNMDEH/TK | 1 |
|  |  |  |  | 2F | 1ST-ROOM-01_1 | AM071KN4DEH/TK | 5 |
|  |  |  |  | 2F | 1ST-ROOM-03 | AM036FNNDEH/TK | 2 |
|  |  |  |  | 2F | 1ST-ROOM-03 | AM045FN4DEH/TK | 2 |
|  |  |  |  | 2F | 1ST-ROOM-05 | AM112FNMDEH/TK | 1 |
|  |  | AM300KXVAGH/TK | 1 | 2F | 1ST-ROOM-06 | AM022FNQDEH/TK | 2 |
|  |  |  |  | 2F | 1ST-ROOM-11 | AM090FNMDEH/TK | 1 |
|  |  |  |  | 1F | GR-ROOM-01_1 | AM071KN4DEH/TK | 2 |
|  |  |  |  | 1F | GR-ROOM-02 | AM056KN4DEH/TK | 3 |
|  |  |  |  | 1F | GR-ROOM-03 | AM036FNNDEH/TK | 2 |
|  |  |  |  | 1F | GR-ROOM-05 | AM022FNQDEH/TK | 1 |
|  |  |  |  | 1F | GR-ROOM-06 | AM056FN4DEH/TK | 1 |
|  |  |  |  | 1F | GR-ROOM-08 | AM045FN4DEH/TK | 2 |
|  |  |  |  | 1F | GR-ROOM-10 | AM022FNTDEH/TK | 1 |
|  |  |  |  | 1F | GR-ROOM-11 | AM112FNMDEH/TK | 1 |
| Total of Outdoor Units |  |  | 3 | Total of Indoor Units |  |  | 50 |

Table ( 2.18): Outdoor And Indoor Nominal Capacity [kW]

| Name | Model name | ID Type | Nominal Capacity Cooling [kW] | Nominal Capacity Heating [kW] | Dimension [Mm] | Qty. |
| --- | --- | --- | --- | --- | --- | --- |
| 3RD-ROOM-01 | AM090KN4DEH/TK | 360 Cassette | 9 | 10 | 947x281x947 | 3 |
| 3RD-ROOM-02 | AM045KN4DEH/TK | 360 Cassette | 4.5 | 5 | 947x281x947 | 1 |
| 3RD-ROOM-04 | AM045FNNDEH/TK | 4Way CASSETTE (600 x 600) | 4.5 | 5 | 575x250x575 | 2 |
| 3RD-ROOM-05 | AM036FNNDEH/TK | 4Way CASSETTE (600 x 600) | 3.6 | 4 | 575x250x575 | 1 |
| 3RD-ROOM-07 | AM028FNNDEH/TK | 4Way CASSETTE (600 x 600) | 2.8 | 3.2 | 575x250x575 |  |
| 3RD-ROOM-06 | AM022FNTDEH/TK | Neo Forte | 2.2 | 2.5 | 825x285x189 | 1 |
| 3RD-ROOM-08 | AM045FN4DEH/TK | 4Way Cassette S | 4.5 | 5 | 840x204x840 | 1 |
| 2ND-ROOM-01_1 | AM071KN4DEH/TK | 360 Cassette | 7.1 | 8 | 947x281x947 | 4 |
| 2ND-ROOM-02 | AM022FNQDEH/TK | Neo Forte | 2.2 | 2.5 | 825x285x189 | 2 |
| 2ND-ROOM-03 | AM056FNNDEH/TK | 4Way CASSETTE (600 x 600) | 5.6 | 6.3 | 575x250x575 | 1 |
| 2ND-ROOM-04 | AM036FNNDEH/TK | 4Way CASSETTE (600 x 600) | 3.6 | 4 | 575x250x575 | 3 |
| 2ND-ROOM-06 | AM112FNMDEH/TK | MSP Duct | 11.2 | 12.5 | 1150x320x480 | 1 |
| 2ND-ROOM-12 | AM045FNNDEH/TK | 4Way CASSETTE (600 x 600) | 4.5 | 5 | 947x281x947 | 1 |
| 2ND-ROOM-14 | AM090FNMDEH/TK | MSP Duct | 9 | 10 | 1150x260x480 | 1 |
| 1ST-ROOM-01_1 | AM071KN4DEH/TK | 360 Cassette | 7.1 | 8 | 947x281x947 | 5 |
| 1ST-ROOM-03 | AM036FNNDEH/TK | 4Way CASSETT E (600 x 600) | 3.6 | 4 | 575x250x575 | 2 |
| 1ST-ROOM-03 | AM045FN4DEH/TK | 4Way Cassette S | 4.5 | 5 | 840x204x840 | 2 |
| 1ST-ROOM-05 | AM112FNMDEH/TK | MSP Duct | 11.2 | 12.5 | 1150x320x480 | 1 |
| 1ST-ROOM-06 | AM022FNQDEH/TK | Neo Forte | 2.2 | 2.5 | 825x285x189 | 2 |
| 1ST-ROOM-11 | AM090FNMDEH/TK | MSP Duct | 9 | 10 | 1150x260x480 | 1 |
| GR-ROOM-01_1 | AM071KN4DEH/TK | 360 Cassette | 7.1 | 8 | 947x281x947 | 2 |
| GR-ROOM-02 | AM056KN4DEH/TK | 360 Cassette | 5.6 | 6.3 | 947x281x947 | 3 |
| GR-ROOM-03 | AM036FNNDEH/TK | 4Way CASSETTE (600 x 600) | 3.6 | 4 | 575x250x575 | 2 |
| GR-ROOM-05 | AM022FNQDEH/TK | Neo Forte | 2.2 | 2.5 | 825x285x189 | 1 |
| GR-ROOM-06 | AM056FN4DEH/TK | 4Way Cassette S | 5.6 | 6.3 | 840x204x840 | 1 |
| GR-ROOM-08 | AM045FN4DEH/TK | 4Way Cassette S | 4.5 | 5 | 840x204x840 | 2 |
| GR-ROOM-10 | AM022FNTDEH/TK | Neo Forte | 2.2 | 2.5 | 825x285x189 | 1 |
| GR-ROOM-11 | AM112FNMDEH/TK | MSP Duct | 11.2 | 12.5 | 1150x320x480 | 1 |

2.8  Mechanical Ventilation :

Ventilation is the process of supplying and removing air by natural or mechanical means to and from a building. The design of a building’s ventilation system should meet the minimum requirements of the building (Ventilating Systems) regulations.

There are two ways for Ventilation:

- “Natural ventilation” covers uncontrolled inward air leakage through cracks, windows, door ways and vents (infiltration) as well as air leaving a room (exfiltration) through the same routes. Natural ventilation is strongly affected by weather conditions and is often unreliable.

- Mechanical or forced ventilation is provided by air movers or fans in the wall, roof or air conditioning system of a building. It promotes the supply or exhaust air flow in a controllable manner.

The air flow rate into a room space, for general mechanical supply and extract systems, is usually expressed in:

- Air changes per hour

- An air flow rate per person

- An air flow rate per unit floor area

An air change per hour (ACH) is the most frequently used basis for calculating the required airflow. Air changes per hour are the number of times in one hour an equivalent room volume of air will be introduced into, or extracted from the room space.

| Table (2.19) : Ventilation rate |  |  |  |
| --- | --- | --- | --- |
| Room | Volume(m³) | Ventilating Rate |  |
|  |  | (L/s) | (CFM) |
| Kitchen | 22.92 | 63.5 | 134.6 |
| Man Toilet | 9.67 | 26.8 | 56.4 |
| Woman Toilet | 9.67 | 26.8 | 56.4 |
| Handicapped toilet | 13.69 | 37.9 | 80.4 |

Type of suction fan is TOSHEPA WALL VENTILATOR VRH-30S1which have the following specifications :

- AC 220 V/ 50 Hz.

- Plastic body and blades.

- 2 directions .

- Easy for cleaning.

- Safety back window.

- More than 5000 working