3.1 Introduction

Plumbing is the art and science of installing pipes in buildings, fixtures and other appurtenances for bringing in the water supply and removing liquid and waterborne wastes. Plumbing systems are one of the most important parts of building design because it's prevent transmission of disease, hygiene, remove the dirty water and etc.

Plumbing includes many systems in buildings, the figure below shows the details of the plumbing systems.

Plumbing Systems

Figure (3.1): Plumping systems types

Grey water treatment which means all wastewater that is discharged from a building excluding black water. This includes water from lavatories and kitchen sinks.

The main purpose of grey water recycling and treatment is to substitute the precious drinking water in applications which do not require drinking water quality ; with grey water recycling it is possible to reduce the amounts of fresh water consumption as well as wastewater production in addition to reducing the water bills.

In water treatment the main process is using the sand filter to achieve the required percentage of recycled water.

3.2 Water supply system

3.2.1	Overview

There are two types of water distribution systems for buildings:

- Up feed distribution system.

- Down feed distribution system.

The system that we will be use to this building is Down feed distribution system.

the system which operates by pumping the water from the city main or suction tank at the ground floor to a roof tank from which the fixture units are fed .

The design of main water supply for the building needs to take into consideration the actual and anticipated future consumption. Moreover , size of water main pipe, and required pressure of water are essential .

3.2.2  Calculations of  hot and cold water supply systems :

To determine the pipe size for cold and hot water supply system , the water  supply fixture unit (WSFU) for each fixture unit must be determined and total fixture unit on each piping run out be calculated, the minimum flow pressure required at the critical fixture unit must be determined.

There is one fixture unit (kitchen sink) (WSFU) as follow:

Figure (3.2): Sample WSFU

- kitchen sink: is a fixture unit needs cold and hot water supplies as shown in Table A(3.3)  the value Fixture Units of the kitchen sink  for a public use is (4) , while the daily use is not too much will take the private use Fixture Units (2).

Or hot water only was needed then this value should be multiplied by (3/4), so the demand of the kitchen sink will be as follow:

        - (2 ) WSFU for both hot and cold water demand.

        - (3/4)×2  WSFU for hot or cold water only.

- Water closet: is a fixture unit needs cold supplies , the value of Fixture Units of the Water closet for General use is (5 ).

- Lavatory: is a fixture unit needs cold and hot water supplies , the value Fixture Units of the lavatory for General use is (2) , while if cold or hot water only was needed then this value should be multiplied by (3/4), so the demand of the Toilet will be as follow:

  - Fixture Units (2) for both hot and cold water demand.

b.   (3/4)×2 Fixture Units for hot or cold water only .

| Table (3.1): The Fixture Unit load |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Fixture unit | No. Of Fixture | WSFU | WSFU cold water | WSFU hot water | No. of FU hot ,cold |
| Kitchen Sink | 1 | 34×2 | 1.5 | 1.5 | 2 |
| Lavatory (general) | 3 | 34×2 | 4.5 | 4.5 | 6 |
| Water Closet (cleaning) | 3 | 2 | 6 | 0 | 6 |
| ∑ WSFU | 7 | --- | 12 | 6 | 14 |

The amount of water supply fixture unit cold water is 12 fixture unit load so we use the Table A(3.3) for estimating demand to calculate the required amount of water which is equal (9.2) gallon per minute (gpm) by using the interpolation.

| Table (3.2): The load of Fixture Units and Demand (gpm) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. Of Floors | Zone | Load, WSFU |  |  | Demand, (gpm) |  |  |
|  |  | Cold water | Hot water | Hot , Cold water | Cold water | Hot water | Hot , Cold water |
| Ground | B | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
| First | B | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
| Second | A | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
|  | B | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
| Third | A | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
|  | B | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
| Fourth | A | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
|  | B | 12 | 6 | 14 | 9.2 | 5 | 10.4 |
| Total | -- | 96 | 48 | 112 | 73.6 | 40 | 83.2 |

3.2.3 Pipe size calculations:

Using Down feed distribution system where the water from the gravity tank on the roof serves the floor below by gravity system .

In this system , the static pressure will be the main pressure , and the equation of flow will be  :

Static pressure=Friction head loss+ Minimum flow pressure…….……........…(3.1)

    - Using the Table A(3.1) Minimum pressure required by typical plumbing fixture and the (kitchen sink) is the critically fixture unit, the minimum flow pressure is (8 )psi.

static pressure = 8m×1ft0.3048m×0.433Psi1ft=11.36 Psi

Friction Head Loss = Static pressure - Min. Flow Pressure

=11.36 -8=3.36 Psi

Equivalent Length = 35 m×1ft0.305m=114.829ft

TEL = 114.829×1.5=172.2ft

Then :

friction head loss=∆PTEL=3.36 psi ×100(172.2)×100ft=1.95 Psi/100ft

Table (3.3): Size of cold water pipes

It possible to choose the pipes size from above Table (3.3 ) , or by using the chart from figure (3.1) Appendix  B  of  Friction Head Loss for Water in commercial Steel Pipe (Schedule 40) .

Figure (3.3): Cold Water Riser

*See the (figure 3.25 in Appendix B) Cold water Riser

Table (3.4) : The total calculation for The Risers

| No. Of Floor | ZONE A |  |  | ZONE B |  |
| --- | --- | --- | --- | --- | --- |
|  | Total no. Of FU For cold | Total no. Of FU for hot |  | Total no. Of FU For cold | Total no. Of FU for hot |
| Ground | 0 | 0 |  | 12 | 6 |
| First | 0 | 0 |  | 12 | 6 |
| Second | 12 | 6 |  | 12 | 6 |
| Third | 12 | 6 |  | 12 | 6 |
| Fourth | 12 | 6 |  | 12 | 6 |
| ∑ WSFU | 36 | 18 |  | 60 | 30 |
| ∑ WSFU for cold | 96 fu | 73.6 gpm= |  | 16.7 m³/h = | = 4.64 l/s |
| ∑ WSFU for hot | 48 fu | 40 gpm= |  | = 9.08 m³/h | = 2.52 l/s |

Convert from gpm to m³/hr

∑ WSFU for cold water Riser = 73.6galonminute×0.227124707m3hr

=16.7m³/h

∑ WSFU for hot = 40galonminute×0.227124707m³hr=9.08m³/h

The total amount of water required which is 73.6 gpm about 16.7 m³/h for cold water Riser and 40 gpm about 9 m³/h for hot water supply Riser .

| Table (3.5) : Properties of cold water Riser |  |  |  |  |
| --- | --- | --- | --- | --- |
| Riser with two zone | WSFU | GPM | Diameter[Inch] | Velocity [fps] |
|  | 96 | 73.6 | 2 1/2 | 4 |

| Table (3.6) : Properties of hot water riser |  |  |  |  |
| --- | --- | --- | --- | --- |
| Riser with two zone | WSFU | GPM | Diameter[Inch] | Velocity [fps] |
|  | 48 | 40 | 2 | 3 |

Figure (3.4): Hot Water Risers and Solar Heating System

*See the (figure 3.26 in Appendix B) Hot water Supply Riser .

The total water supply fixture unit for cold water risers equal 96 WSFU and for hot water risers equal 48 WSFU.

The total demand for cold water equals (73.6) gpm and the total demand for hot water equals (40)gpm .

The friction loss is 1.95 Psi/100ft

So the pipe diameter of the main pump is 2 1/2" and the velocity is 4 fps.

3.3 Hot Water System Recirculation :

When do not use hot water, the water in any Pipes will lose heat and you must be work of Cycling a certain amount of water, Even this water remains valid for use. To find this amount must know the rate of heat loss in pipes, and get it from the following Table:

| Table (3.7) : Approximate insulated piping heat loss and surface Temperature : |  |  |  |
| --- | --- | --- | --- |
| Nominal Pipe size (In.) | Insulation Thickness (In.) | Heat Loss (Btu/h/linear ft) | Surface Temperature (°F) |
| 1/2 | 1 | 8 | 68 |
| 3/4 | 1 | 10 | 69 |
| 1 | 1 | 10 | 69 |
| 1 1/4 | 1 | 13 | 70 |
| 1 1/2 | 1 | 13 | 69 |
| 2 or less | 1/2ª | 24 or less | 74 |
| 2 | 1 | 16 | 70 |
| 2 1/2 | 1 1/2 | 12 | 67 |
| 3 | 1 1/2 | 16 | 68 |
| 4 | 1 1/2 | 19 | 69 |
| 6 | 1 1/2 | 27 | 69 |
| 8 | 1 1/2 | 32 | 69 |
| 10 | 1 1/2 | 38 | 69 |

Figure (3.5): Hot Water System Recirculation

3.3.1. Calculation for Return pipes diameter :

Recirculating systems are usually provided when piping run is about 100 ft long.

The types of recirculation systems :

- Thermo siphon recirculation system .

- Forced circulation system : (low and long buildings ) controlled pump is used .

Choose the second system to provide maximum hot water demand immediately at required temperature .

: Recirculation system includes

- Hot water supply piping

- Hot water return piping

- Circulating pumps

- Balance valves

- Shut off valves

- Check valves

- Controls for the pumps

Figure (3.6): Up feed Hot Water System with Heater at Bottom of    System

*See Figure (3.27) at Appendix B ( Hot Water Riser Return)

- Return pipe diameter=1/2 supply pipe diameter

- Heat loss(return)=2/3 Heat loss(supply):

Heat loss(supply)=EL*Heat loss.

Heat loss from Table:(3.6)=16 btu/hr for dimeter 2".

EL for riser (1)=3.35+(3.85*4)+(20)= 38.75/0.3048=127.13 ft.

127.13 ft *16 btu/h/ft linear =2034.12 btu/h

Heat loss(return)=2/3 *2034.12=1356 btu/h

Total heat losses =2034.12+1356=3390 btu/h

By using this equation:

10,000 btu/h Heat loss=1GPM(circulated pump)

circulated pump=0.3390 GPM

| Table (3.8) : Properties of Riser (Recirculation) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Section No. | EL [ft] | Supply Diam. Inch | Return in Diam. Inch | Heat Loos supply | Heat Loss return [Btu/h] | Total heat loss [Btu/h] | Circula-ted pump [GPM] |
|  |  |  |  | [Btu/h] |  |  |  |
| Main Riser | 127 | 2 | 2 | 127*16=2032 | 2023*2/3=1354.6 | 3390 | 0.3390 |
| Section A-4th level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section B-4th level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section A-3rd level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section B-3rd level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section A-2nd level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section B-2nd level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section B-1st level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
| Section B-Gr.level | 52 | 1.5 | 3/4 | 52*13=676 | 676*2/3=450.66 | 1126.66 | 0.1127 |
|  |  |  |  | ∑TOTAL |  | 12390.94 | 1.2394 |

3.4  Selections :

3.4.1 Selection for cold water pump :

In order to choose the details of the required water pump we have to determine two main conditions, the amount of total flow rate of demand water and the total head:-

- Flow rate determination:

According to the previews calculation and equation estimation, the total flow rate for the riser is 73.6 gpm, so by converting 73.6 gpm equal to 16.7 [m³/h].

- Head estimation

According to the previews calculation and equation estimation the head is 34 psi & equal 2.3 Bar, Adding 1 bar for fittings losses the value is almost 3.3 bar .

Pump selection

Using (dp-select) software and with filling data into brackets as follow :

Figure (3.7) : Pump data

The pump model selected “DPV 25/2 B”.

The characteristic curves of this pump as follow :

Figure (3.8) : Pump Characteristic Curves

3.4.2 Selection for cold water tank :

The main condition in choosing the size of water tank to limit the size with the daily use of demand and number of storage day .

Size Water Tank=Number of people in the building ×Daily consumption for    each person× Number of storage day ……………..(3.2)

- Number of people in the building :

From Table (   ) ASHRAE 62 Estimated maximum occupancy P/1000ft² or 100 m²  is (7) with building application of offices .

Number of people in the building=Area Of BuildingMaximum Area Occupy by one person…(3.3)

=200014=143 person

- Daily consumption for  each person :

From the Uniform Plumbing Code (UPC)  is 20 Gallons per day per employee .

From the Egypt Code :

QAV(Sewerage)=(0.8-0.9)QAV(WATER)

Substitute the sewerage quantities equal of water quantities .

Number of storage day depending on the average schedule distribution program in Hebron about 15 day .

Size Water Tank=143×20× 15=42900 Gallons =162 m³

When  the number of peoples increase by full occupancy about 250 person

Size Water Tank=250×20× 15=75000 Gallons =284 m³

3.4.3  Selection for boiler

The types of Hot Water Heaters :

- Instantaneous water heaters (tank less water heaters )  ;Atmor,Gas boiler :

Units that heat water only when hot water faucet opens or other fixture demands hot water ,They are referred to as tank-less heaters because they do not use any sort of storage tank.

- Tank type water heater:

Are the most common used units .Their advantages are that they makes or provide a large quantity of heated water available upon demand .

the second system of tank type heater use it in this project because need to compensate the hot water demand.

Use Table (A3.9) to calculate the size of the boiler  :

Total Daily consumption =number of person ×Hot water per person  (gal/day)

=254 ×2  =508 (gal/day)

Maximum hourly demand  =maximum hourly demand portion of daily use ×Total

=1/5×508 =101.6 (gal/hr)

Duration of peak load = 2 (hour)

Total peak load =2 hr×101.6 gal/hr =203.2 (gal)

Storage capacity = 1/5×Total =1/5×508 =101.6 (gal)

Convert from gallon to liter to get the size of boiler tank (theoretical calculation:

1 galon = 3.78 liter , 101.6 galon =384.04 liter

Heat capacity = 1/6 ×508 =84.66 (gal)

Recovery Rate=total peak load –(3/4 × average capacity)Duration of peak load

=203.2 –(3/4 × 101.6)2=63.5 galon

The value of 63.5 (galon) should be filled at storage tank when be consumed .

And be less than the value of storage capacity .

Heater Capacity=(GPH×∆T)/410  [Kw]

where:

Q: boiler capacity. [kW]

∆T=70F=difference in temperature between water entering heater

and leaving the heater.

Make up water temperature=50F

Heater Capacity=(101.6×70)/410=17.34  [Kw]

3.4.4  Selection for hot water central Tank size :

In the case of cold water calculation where calculate the demand load gpm by fixture load , but in the case of hot water central use the hot water demand per fixture for type of offices (Gallons of water per hour per fixture ).

| Table (3.9): Fixture Units loads (gph) |  |  |  |
| --- | --- | --- | --- |
| Fixture unit | No. of fixture | Office building (GPH) | GPH for sum. Of fixture |
| Kitchen Sink | 1 | 20 | 20 |
| Lavatory (general) | 3 | 6 | 18 |
| Total | 4 | --- | 38 |

In the table follow show the total calculations for all floors of water demand per fixture .

| Table (3.10): The hot water demand per fixture for all floor (gph) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| No. Of Floors | Zone | Demand, (gph) |  |  |
|  |  | Kitchen Sink | lavatory | Total |
| Ground | B | 20 | 18 | 38 |
| First | B | 20 | 18 | 38 |
| Second | A | 20 | 18 | 38 |
|  | B | 20 | 18 | 38 |
| Third | A | 20 | 18 | 38 |
|  | B | 20 | 18 | 38 |
| Fourth | A | 20 | 18 | 38 |
|  | B | 20 | 18 | 38 |
| Total | -- | 160 | 144 | 304 |

The demand factor for the building type offices is =0.3

The storage capacity factor is = 2

Probablemaxdemand =Possiblemaxdemand×Demand Factor

=304×0.3=91.2 GPH

Storage Tank Capacity=GPH×Demand Factor×Storage Factor….(3.4)

=304×0.3×2=182.4 Gallon=0.69 m³=690 liter

Table (3.11) Hot-Water Demand per Fixture for Various Types of Buildings

(Gallons of water per hour per fixture calculated a final temperature of 140°F

See the technical specification of boiler from Catalogue

3.5 Sanitary drainage system

3.5.1 Drainage system Definition:

The "Sanitary" drainage system carries away the contaminated fluids and solids created at the fixture . The drainage systems of sanitary black water to be treated and remove from the system , but storm and grey water treated and use it again in the system .

3.5.2  Drainage system components:

The main components of drainage system are:

Figure (3.9): Drainage system components

      - Fixture units

      - Trap

      - Clean out

      - Drainage pipe

      - Stack and vent pipes

      - Manholes

      - Septic tank or municipal sewage system

      - Accessories

This project deals with two types of wastewater which is gray and black water, the separation of waste water will rationalize consumption of water and reuse it in irrigation and in flushing water closet.

3.5.3  Sanitary drainage

3.5.3.1   Design procedure and pipe sizing

Pipe size is calculated by using a concept of fixture units (DFU) instead of using gpm of drainage water. This unit takes into account not only the fixtures water use but also its frequency of use, which is the DFU has a built–in diversity factor. This enables us, exactly as for water supply to add DFU of various fixtures to obtain the maximum expected drainage flow. Drainage pipes sized for a particular number of drainage fixture units, according to Tables (3.11), (3.12), (3.14), (3.15) . These tables are built into the fill factors, which are:

      - 50% fill in branches (horizontal pipes)

      - (25-33)% fills in stack (vertical pipes)

      - 50% fill in building and swear drains The recommended velocity for drainage piping:

      - For branches the recommended velocity is 2 ft/s

      - For building pipes the recommended velocity is 3 ft/s

      - For greasy flow the recommended velocity is 4 ft/s Velocity of water flow through   drainage piping depends on:

      - Pipe diameter

      - Slope  Minimum slope requirements for horizontal drainage piping:

      - For pipes of diameter ≤ 3" the minimum slope is 1/4”/ft (2%)

      - For pipes of diameter ≥ 4" the minimum slope is 1/8”/ft (1%)

Design procedure:

- Calculation of the number of DFU for each branch by using Table (A3.12)

- Calculation of the number of DFU for each stack

- Choosing the branch pipe diameter by using Table (A3.14)

- Choosing the stack pipe diameter .

- Comparing the stack pipe diameter with branch diameter

- Choosing the building drain pipe diameter by using Table (3.15)

To achieve the recommended velocities which are 3 fps in building drain, it will be chosen the slope and flow velocity in building drain by using Table A(3.11).

3.5.3.2   Black Water pipe sizing :

The following figure and tables shows the sizing of stacks:

Figure (3.10): Black Water Stacks

*See Figure (3.28) at Appendix B ( Black Water Stacks)

| Table (3.12) : Sizing stack A of black water |  |  |
| --- | --- | --- |
| Stack A | Total dfu values | Diameter (inch) |
| Branch of Fourth floor | 18 | 3 |
| Stack between Fourth and third floor | 18 | 3 |
| Branch of third floor | 18 | 3 |
| Stack between third and second floor | 36 | 3 |
| Branch of second floor | 18 | 3 |
| Stack between second and first floor | 54 | 4 |

| Table (3.13) : Sizing stack B of black water |  |  |
| --- | --- | --- |
| Stack B | Total dfu values | Diameter (inch) |
| Branch of Fourth floor | 18 | 3 |
| Stack between Fourth and third floor | 18 | 3 |
| Branch of third floor | 18 | 3 |
| Stack between third and second floor | 36 | 3 |
| Branch of second floor | 18 | 3 |
| Stack between second and first floor | 54 | 3 |
| Branch of first floor | 18 | 3 |
| Stack between first and ground floor | 72 | 3 |
| Branch of ground floor | 18 | 3 |
| From ground floor to building drain (stack) | 90 | 4 |

| Table (3.14) :Sizing of black water stacks and building drain. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Stack | Total Dfu | Diam. (in) | Diam. building drain | Slope % | Velocity ft/s |
| A | 54 | 4 | 4 | 1/8 | 1.93 |
| B | 90 | 4 | 4 | 1/4 | 2.73 |

Stack  A: one stack of three branch Intervals.

Stack  B: one stack with more than three branch Intervals.

3.5.3.3   Grey Water pipe sizing :

Figure (3.11): Gray Water Stacks

*See Figure (3.29) at Appendix B ( Grey Water Stacks)

| Table (3.15) : Sizing stack B of Grey water |  |  |
| --- | --- | --- |
| Stack B | Total dfu value | Diameter (inch) |
| Branch of Fourth floor | 6 | 2 |
| Stack between Fourth and third floor | 6 | 2 |
| Branch of third floor | 6 | 2 |
| Stack between third and second floor | 12 | 2 |
| Branch of second floor | 6 | 2 |
| Stack between second and first floor | 18 | 2 |
| Branch of first floor | 6 | 2 |
| Stack between first and ground floor | 24 | 2 |
| Branch of ground floor | 6 | 2 |
| From ground floor to building drain (stack) | 30 | 3 |

| Table (3.16) : Sizing stack A of Grey water |  |  |
| --- | --- | --- |
| Stack A | Total dfu value | Diameter (inch) |
| Branch of Fourth floor | 6 | 2 |
| Stack between Fourth and third floor | 6 | 2 |
| Branch of third floor | 6 | 2 |
| Stack between third and second floor | 12 | 2 |
| Branch of second floor | 6 | 2 |
| Stack between second and first floor | 18 | 3 |

| Table (3.17) : Sizing of Grey water stacks and building drain. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| stack | Total dfu | Diameter of stack (in) | Diam. building drain | Slope % | Velocity ft/s |
| A | 18 | 3 | 3 | 1/4 | 2.25 |
| B | 30 | 3 | 4 | 1/4 | 2.25 |

Stack A: one stack of three branch Interval.

Stack B: one stack with more than three branch Interval.

3.6  Manhole design

The main purpose of the manholes is to carry the water from stacks to various drainage points.

This project contains three types of manhole, which is:

      - Sanitary manhole for black water .

      - Sanitary manhole for gray water .

      - Storm Water

The design of the manholes depend on the ground and its nature around the building, and so as the first manhole height should not be less than 50 cm, and the depth of the other manholes will depend on the distance between the manholes and the slope of the pipe that connecting them.

According to the table below, it will be estimated the diameter of the manhole according to their depth.

Table  (3.18) : Diameter of the manhole according to their depth

| Depth | Diameter |
| --- | --- |
| 70-80 | 60 |
| 80-140 | 80 |
| 140-250 | 100 |
| 250-∞ | 125 |

3.6.1 Manhole calculation

Using the following  equations to size manholes (depth ,invert level and diameter of manholes by the standards of civil works ):

        - Depth: (M2 = M1 + (Slope × Distance) + 5 + Level Difference) in cm……(3.5)

        - Top level: Manholes face level on the ground

        - (Invert level = Top level - Depth) in m

        - Outlet level = - (Depth - 0.05) in m

The figure below shows the details of the manholes:

Figure 3.12: Manholes details

The result calculation of the grey water and black water manholes is listed in the tables below:

| Table (3.19):Black water manholes |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Manh. No. | Top level (m) | Invert level (m) | Outlet level (m) | Depth cm | Dia. (cm) | Cover Type |
| M01 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |
| M02 | -0.30 | -0.88 | -0.53 | 58 | 60 | Concrete |
| M03 | -0.30 | -1.075 | -0.725 | 77.5 | 60 | Concrete |
| M04 | -0.30 | -1.24 | -0.89 | 94 | 80 | Concrete |
| M05 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |

| Table (3.20):Gray water manholes |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Manh. No. | Top level (m) | Invert level (m) | Outlet level (m) | Depth cm | Dia. (cm) | Cover Type |
| M01 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |
| M02 | -0.30 | -0.87 | -0.52 | 57 | 60 | Concrete |
| M03 | -0.30 | -0.945 | -0.595 | 64.5 | 60 | Concrete |
| M04 | -0.30 | -1.155 | -0.805 | 85.5 | 80 | Concrete |
| M05 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |
| M06 | -0.30 | -0.88 | -0.53 | 58 | 60 | Concrete |
| M07 | -0.30 | -1.00 | -0.65 | 70 | 60 | Concrete |
| M08 | -0.30 | -1.10 | -0.75 | 80 | 80 | Concrete |
| M09 | -0.30 | -1.55 | -1.2 | 1.25 | 80 | Concrete |
| M10 | -0.30 | -1.55 | -1.2 | 1.25 | 80 | Concrete |
| M11 | -0.30 | -1.55 | -1.2 | 1.25 | 80 | Concrete |

From the last Manhole to grey water septic tank , install filter and pump to rise the grey water to Roof tank ( of grey water) to feed the water closet flush tank.

3.7 Storm drainage

Every structure shall be provided with a storm drainage system that will conduct storm water from roofs and all paved areas into an approved sewer system . the storm water drainage system within or on a building must be completely separate from the sanitary drainage system.

The  design  of  the  rain  collection  piping,  whether  exterior  gutters,  and  leaders,  or  interior conductors and drain depends upon three factors:

    - The amount of rain fall in a specified period of time.

    - The size of the area being drained.

    - The degree of pipe fill, that is whether a pipe or gutter runs 50%, 33% or 100% fill .

The roof area of this building is 400 m² ,and therefore needs  4'' FD.

| Table (3.21):Storm Water Manholes |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Manh. No. | Top level (m) | Invert level (m) | Outlet level (m) | Depth cm | Dia. (cm) | Cover Type |
| M01 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |
| M02 | -0.30 | -0.86 | -0.51 | 56 | 60 | Concrete |
| M03 | -0.30 | -0.80 | -0.45 | 50 | 60 | Concrete |
| M04 | -0.30 | -1.02 | -0.67 | 72 | 60 | Concrete |
| M05 | -0.30 | -1.14 | -0.79 | 84 | 80 | Concrete |
| M06 | -0.30 | -1.21 | -0.86 | 91 | 80 | Concrete |
| M07 | -0.30 | -1.55 | -1.20 | 1.25 | 80 | Concrete |
| M08 | -0.30 | -1.55 | -1.20 | 1.25 | 80 | Concrete |

Figure (3.13): Storm Water Leader

*See Figure (3.30) at Appendix B ( Storm Water Leaders)