## Slide 1: بِسْمِ اللهِ الرَّحْمنِ الرَّحِيمِ
Design Of Mechanical System For A Hotel Building In Hebron City
Done By:
Mohammad Abusarhan Mahmoud zyoud
Supervisor:
Eng.kazem osaily

## Slide 2: Project outline
Chapter one: Introduction
Includes an overview, the project objectives and time table .
chapter two: Heating load
Includes a sample calculation for one room in details and the other rooms loads.
Chapter three : Cooling load
Includes a sample calculation for one room in details and the other rooms loads

## Slide 3
Chapter four: Plumbing System
Includes the calculation of water supply system to determine the total required amount of water and the drainage system.
Chapter five: Firefighting System
Design a suitable firefighting system that covers the requirements of the building.
Chapter six: Refregrators
Theoretical calculations and design a Refregerator and Freezer

## Slide 4: Task Description first semester

## Slide 5: Time Table second semester

## Slide 6: Project description
The total area of the project 9100 (m²) .
The number of people who can serve them are 180 person .

## Slide 7: Site plan of the project

## Slide 8: Objectives that have been achieved
Design the mechanical systems inside the hotel building
Theoretical calculations and design of HVAC system
Theoretical calculations and design of plumping system
Theoretical calculations and design of refregerators
Notes: erators

## Slide 9: ASHRAE Comfort Chart
Properties of Atmosphere Air:-
a) Dry Bulb (db) Temperature
b) Specific and Relative Humidity
c) Wet Bulb Temperature (wb)
d) Dew-Point Temperature

## Slide 10: Overall Heat Transfer Coefficients
U =
 | Material | ΔX(m) | k(W/m.°C) | R(m2./W)
1 | limestone | 0.05 | 2.2 | 0.022
2 | Concrete | 0.15 | 1.75 | 0.085
3 | polyurethane | 0.03 | 0.04 | 0.750
4 | Cement brick | 0.07 | 0.9 | 0.07
5 | Plaster | 0.03 | 1.4 | 0.02
 | Material | ΔX(m) | k(W/m.°C) | 
1 | limestone | 0.05 | 2.2 | 0.022
2 | Concrete | 0.15 | 1.75 | 0.085
3 | polyurethane | 0.03 | 0.04 | 0.750
4 | Cement brick | 0.07 | 0.9 | 0.07
5 | Plaster | 0.03 | 1.4 | 0.02

## Slide 11: HVAC System Heating Load

## Slide 12: Cooling Load

## Slide 13: This table shows the total cooling loads for the project
Floor | Q(kW)
Ground | 117.1
First | 64.7
Second | 112.64
Third | 112.64
Fourth | 71.45

## Slide 14: Heating Load calculation
Rate of heat transfer from the walls, ceiling and ground :-
Q = U × A × (Tin – Tout)
Rate of heat transfer from the doors and windows:
Q = U × A × (Tin – Tout)
Heat loss due to infiltration:
Q infiltration = ṁ × (h ̥ - hi ).
Heat gain due to ventilation:
Q ventilation = ṁ × (h ̥ - hi ).

## Slide 15: This table shows the total heating loads for the project
Floor | Q(kW)
Ground | 82.3
First | 31.6
Second | 76
Third | 76
Fourth | 37.5

## Slide 16: VRF System Variable refrigerant flow (VRF) is an air-condition system configuration where there is one outdoor condensing unit and multiple indoor units.

## Slide 17: VRF SYSTEM out door units for ground floor
Unit | Cooling Load (HP) | Cooling load (kW ) | Outdoor Unit Name | Dimension
Unit g-1 | 22 | 317.3 | - | (880x1703x765)x2
Unit g-2 | 22 |  | - | (880x1703x765)x2
Unit g-2 | 22 |  | - | (880x1703x765)x2
Unit g-2 | 22 |  | - | (880x1703x765)x2

## Slide 18: VENTALATION

## Slide 19: Plumbing System
Consists of two parts : 1ـ Water Supply System. 2- Drainage System .

## Slide 20: Water Supply System
There are two basic types of water distribution systems for building .
Up feed
distribution system.
Down feed
distribution system.

## Slide 21: Water Supply System
Network of pipes that transport hot and cold potable water under pressure
Fixture – A device that uses water
(sink, toilet, dishwasher, etc.).
Water Heater – Large insulated tanks
that heat cold water to be distributed
in the hot water supply lines.

## Slide 22: Water Supply System
Water Main – Supply pipe installed and
maintained by a public entity and on
public property.
Water Service – Pipe from the water main to the
building supply pipes.
Water meter – Measures the amount of water
transported through water service.
Valve – A fitting used to control water flow
(located next to the meter).
MAIN

## Slide 23: Calculations of Water Supply
Main pressure = static head + flow pressure + friction pressure .
Total equivalent length (TEL)
TEL = longest run × 1.5
minimum flow pressure at the critical fixture .

## Slide 24: Size the pipe from chart of steel pipe .

## Slide 25: Table shows the sizing pipe for cold Water
No. of Riser | Total WSFU | Total gpm | Diameter (inch) | Velocity (fps)
First riser | 147 | 54.4 | 2" | 4
Second | 134 | 51.8 | 2" | 4
Third | 84 | 40 | 2" | 4
Fourth | 62 | 33.6 | 2" | 4
Fifth | 43 | 26.2 | 1.5" | 4
Sixth | 41 | 25.4 | 1.5" | 4
Seventh | 41 | 25.4 | 1.5" | 4
Eighth | 66 | 34.8 | 2" | 4
Ninth | 66 | 34.8 | 2" | 4

## Slide 26: Table shows the sizing pipe for hot Water
No. of Riser | Total WSFU | Total gpm | Diameter (inch) | Velocity (fps)
First riser | 59 | 32.6 | 2" | 4
Second | 54 | 30.6 | 1.5" | 4
Third | 42 | 25.8 | 1.5" | 4
Fourth | 37 | 23.5 | 1.5" | 4
Fifth | 34 | 22 | 1.5' | 4
Sixth | 29 | 19.4 | 1.25" | 4
Seventh | 29 | 19.4 | 1.25" | 4
Eighth | 56 | 31.4 | 2" | 4
Ninth | 56 | 31.4 | 2" | 4

## Slide 27: Drainage System
There are two basic types
of drainage systems
for building .
Sanitary drainage .
Storm drainage .

## Slide 28: Sanitary drainage
This system works to
disposal of waste water
resulting from the fixtures .
This system will help
reduce the pollution of
the environment

## Slide 29: Contains:- Sanitary drainage system
Fixture – A device that uses water
(sink, toilet, dishwasher, etc.)
Soil, waste, and vent pipes
Drain and sewer

## Slide 30: sanitary drainage Calculations of
Calculate drainage fixture unit values for various plumbing fixtures .

## Slide 31: Calculate horizontal fixture branches and stacks from table :

## Slide 32: Table shows the pipe size for stack1 and branch .
Stack 1 | Total dfu value | Diameter (inch)
From Fourth floor (branch) | 12 | 4
From Fourth to third floor (stack) | 12 | 4
From third floor (branch) | 4 | 4
From third floor to second floor (stack) | 16 | 4
From second floor (branch) | 4 | 4
From second floor to first floor (stack) | 20 | 4
From first floor (branch) | 36 | 4
From first floor to ground(stack) | 56 | 4
From ground floor (branch) | 24 | 4
From ground floor to building drain (stack) | 80 | 4

## Slide 33: Manholes Depth: (M2 = M1 + (Slope × Distance) + 5 + Level Difference) in cm Top level: Manholes face level on the ground Invert level = (top level – depth) in m outlet level = (depth – 0.05) in m

## Slide 34: Fire fighting system

## Slide 35
Type of firefighting system :-
Fire extinguishers.
Fire hose reels.
Fire hydrant systems.

## Slide 36
Fire extinguishers.

## Slide 37
Fire hose reels.

## Slide 38
Fire hydrant systems.