## Slide 1: Smart Grid Design
Asia Rawashdeh.
Sahar Adem.
Done By:
Supervisor:
Dr. Fouad Zaro.

## Slide 2: Outline:
Objectives.
Introduction.
Practical Investigations.
MATLAB Simulation.
Smart Meters.
Case Study.
Monitoring System.

## Slide 3: objectives:
Practical investigation carried out in smart grid lab and JDECo. company lab.
Design a module for each experiment using MATLAB SIMULINK.
Take a look on smart meters that are used in smart grids and their control software.
Design a grid with its components to be a case study on smart meters and analyze results.
Monitoring System for the designed grid.

## Slide 4: Traditional grid

## Slide 5
Smart grid

## Slide 6: Practical investigations
Practical investigation carried out in Smart Grid Lab and JDECo. Company Lab.
Scenarios:
At Each Time:
Renewable energy source with grid are supplying.
Distributed Generation alone.
Grid is only supplying load.

## Slide 7: Explanations
JDECo. Company Lab

## Slide 8
Components:
JDECo. Company Lab
250 W PV Cell = 2500 W Station
4 Series Batteries = 1 KW
3000 VA Hybrid Inverter
Grid Lines
750 W Pure R Load

## Slide 9: Diagram
JDECo. Company Lab
Components:
2250 W PV Station + 1 KW Batteries.
Hybrid Inverter.
Grid.
750 W Pure R Load
1
2
3
4
1
2
3
4

## Slide 10
Practical Results On

## Slide 13
Case 1
2250 W
1000 W
750W Pure R
240 V 3.04 A

## Slide 14
Case 1 Results
Hybrid
Oscilloscope
Voltmeter & Clamp meter
23.6 V*10
240 V
3.04 A

## Slide 15
Case 2
2250 W
1000 W
750W Pure R
228 V 2.97A

## Slide 16
Case 2 Results
Hybrid
Oscilloscope
Voltmeter & Clamp meter
22.8 V*10
228 V
2.97 A

## Slide 17
Case 3
750W Pure R
1000 W
2250 W
234 V 2.91 A

## Slide 18
Case 3 Results
Hybrid
Oscilloscope
Voltmeter & Clamp meter
23.6 V*10
234 V
2.91 A

## Slide 19: Simulation
JDECo. Company Lab

## Slide 20
1st of Nov Irradiance & Temp
Actual
SIMULINK
Irrad
Temp

## Slide 21
PV at 765 W/ m2 & 26 C
4 Series Batteries with Boost
JDECo. Company Lab

## Slide 22
Grid with Load
JDECo. Company Lab
240 Vrms, 340 V peak
3 Arms, 4.3 A peak

## Slide 23
JDECo. Company Lab

## Slide 24
Case 1 Results
Both Grid and PV are Connected
Approx. 340 V Peak
Approx. 4.3 A Peak
Approx. 240 V RMS
Approx. 3.04 A RMS

## Slide 25
Case 2

## Slide 26
Case 2 Results
PV is Connected
Approx. 310 V Peak
Approx. 4.1 A Peak
Approx. 219 V RMS
Approx. 2.9 A RMS

## Slide 27
Case 3

## Slide 28
Case 3 Results
Grid is Connected
Approx. 340 V Peak
Approx. 4.5 A Peak
Approx. 240 V RMS
Approx. 3.1 A RMS

## Slide 29
Power Flow ETAP 16

## Slide 30: Explanations
Smart Grid Lab

## Slide 31
Components:
1500 W Induction Generator
Grid Lines
90 W PV Cell with 360 W 1 Phase Inverter
300 W 3 Phase Load
Smart Grid Lab

## Slide 32: Diagram
1
Smart Grid Lab
Components:
2
3
Power Sources.
Transmission and Meters.
Load.
1
2
3

## Slide 33
Experiment

## Slide 34
1500 W
360 W
300 W
286 W
117 W
11 W
172 W
Experiment

## Slide 35
Results

## Slide 36: Simulation
Smart Grid Lab

## Slide 37
Induction Generator with Internal Design
Smart Grid Lab

## Slide 38
Induction Generator with Speed as Input
Smart Grid Lab
1300 RPM

## Slide 39
Induction Generator with Torque as Input
Smart Grid Lab
8.7 N.M

## Slide 40
Smart Grid Lab

## Slide 41
Case 1
Approx. 325 V Peak
Approx. 0.65 A Peak
Approx. 0.46 A RMS
Approx. 230 V RMS

## Slide 42
Smart Grid Lab

## Slide 43
Case 2
Approx. 222 V RMS
Approx. 315 V Peak
Approx. 0.42 A RMS
Approx. 0.6 A Peak

## Slide 44
Power Flow By ETAP 16

## Slide 45: Smart Meters and Meter Data Management

## Slide 46
Smart Meters
Provided By PowerCom Company.
Single or 3 Phase, PCR421(single phase), PCR423 (three phase) .
Approved By:
IEC62052.
MID (Measuring Instruments Directive).
SABS (South African Bureau of Standards).
STS (Standard Transfer Specification).
ISO (International Organization for Standardization).

## Slide 47
Smart Meters
PCCG340, concentrator (Computing unit).
Can send commands to the sensors as well as sends tamper alerts to the management system.

## Slide 48
Meter Data Management (MDM)
DCU
Smart Meter

## Slide 49
Smart Meters & MDM
Connection:

## Slide 50
Smart Meters & MDM
As same as previous cases on 750 W pure R load with 2 labs.
Smart meter at the load side.
Command are send.
Message of response was sent.
Results.
Case Study:

## Slide 51
Smart Meters & MDM
Case 1
Relay On.
Commands.
Response Message.

## Slide 52
Smart Meters & MDM
Case 1
Succeeded Commands.
Failed Commands.

## Slide 53
Smart Meters & MDM
Case 1, Results
0.7218 KW.
232.2 V
0.999 PF
49.92 HZ
3.128 A

## Slide 54: Beit Sahour Case Study

## Slide 55
Case Study Description
160 KVA transformer named (302-13) with 60 KW loading.
30 KW PV Station with 21 KW max. generation.
3 feeders with load profile for 2-5 days, calculate max by MATLAB.
1630 W full load losses = 2.7% of full load.
This study is to prove abilities of smart meter in saving energy and prevent thefts.

## Slide 56
Case Study Description
160 KVA Tr-r.
30 KW PV Station.
3 Feeders.

## Slide 57
Case Study Map

## Slide 59
Power Flow of Tr-r = 56.869 KW
Power Flow of PV = 27.1 KW

## Slide 60
Power Losses
Results
Losses Branch | Losses in KW
Main Transformer | 0.225
Under_G2 | 0.027
Under_G3 | 0.077
Under_G1 | 0.001
Over Head 1 | 0.403
Under_G4 | 0.019
Over Head 2 | 0.31
Bundel_3 | 0.021
Bundel_4 | 0.008
Bundel_5 | 0.008
Under_G8 | 0.005
Under_G9 | 0.013
Under_G7 | 0.001
Under_G18 | 0.001
Bundel_2 | 0.001
Losses Branch | Losses in KW
Under_G5 | 0.001
Bundel_6 | 0.108
Under_G10 | 0.001
Under_G11 | 0.003
Under_G12 | 0.001
Bundel_7 | 0.022
Bundel_8 | 0.084
Under_G13 | 0.053
Over Head 3 | 0.048
Under_G14 | 0.001
Over Head 4 | 0.061
Under_G15 | 0.061
Under_G16 | 0.025
Bundel_9 | 0
Under_G17 | 0
Sum | 1.589 KW
1.589/56.869 = 2.7%

## Slide 61: Monitoring System

## Slide 62
Case Study SIMULINK

## Slide 63
Case Study SIMULINK
Zoom to Zone of pole:
302-13-7
Monitoring System Block
Power Flow results are Follows:

## Slide 64
Case Study SIMULINK
Power Flow
results
PV = 27 KW
Tr-r = 56.78 KW

## Slide 65
Case Study SIMULINK
Monitoring Block

## Slide 66
Case Study SIMULINK
Testing:

## Slide 67: Recommendations

## Slide 68
Recommendations:
To develop smart grid lab to be a modernized lab.
JDECo.
Electrical Power Eng. PPU
To look in smart grid lab’s limitations.
Introducing a smart grid lab course for student who are interesting in.
Future Work
Design a smart meter, the project will be in the cooperation with Eng. Mohammed Al-qaisi, and Southern Electricity Company in Dura.
Microgrid controllers can be a powerful project idea.
Complement this project by studying distribution generators.

## Slide 69: Thank You