## Sheet1
Table ( D ) Sanitary Sewer Design Report For Al Burj village( Line D )
Manhole Report | [5 empty] | Pipe Report
Label | Ground Elevation (m) | Rim Elevation (m) | Sump Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (l/s) | Section Shape | Section Size | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 590.83 | 590.83 | 589.13 | 1.2 | 1.7 | P-1 | MH-1 | MH-2 | 41 | 0.069 | Circular | 200 mm | 0.37 | 0.03 | 1.55 | PVC
MH-2 | 589.7 | 589.7 | 587.87 | 1.2 | 1.83 | P-2 | MH-2 | MH-3 | 39 | 0.123 | Circular | 200 mm | 0.44 | 0.03 | 1.68 | PVC
MH-3 | 588.63 | 588.63 | 586.67 | 1.2 | 1.96 | P-3 | MH-3 | MH-4 | 25.5 | 0.163 | Circular | 200 mm | 0.47 | 0.03 | 1.81 | PVC
MH-4 | 587.97 | 587.97 | 585.87 | 1.2 | 2.1 | P-4 | MH-4 | MH-5 | 35 | 0.222 | Circular | 200 mm | 0.45 | 0.02 | 2.29 | PVC
MH-5 | 588.06 | 588.06 | 585.14 | 1.2 | 2.92 | P-5 | MH-5 | MH-6 | 26.5 | 0.292 | Circular | 200 mm | 0.5 | 0.02 | 2.93 | PVC
MH-6 | 587.96 | 587.96 | 584.58 | 1.2 | 3.38 | P-6 | MH-6 | MH-7 | 43.5 | 0.361 | Circular | 200 mm | 0.53 | 0.02 | 3.16 | PVC
MH-7 | 587.05 | 587.05 | 583.68 | 1.2 | 3.37 | P-7 | MH-7 | MH-8 | 28.5 | 0.382 | Circular | 200 mm | 0.54 | 0.02 | 3.1 | PVC
MH-8 | 586.35 | 586.35 | 583.08 | 1.2 | 3.27 | P-8 | MH-8 | MH-9 | 33 | 0.397 | Circular | 200 mm | 0.54 | 0.02 | 2.99 | PVC
MH-9 | 585.53 | 585.53 | 582.39 | 1.2 | 3.14 | P-9 | MH-9 | MH-10 | 39 | 0.412 | Circular | 200 mm | 0.55 | 0.020769 | 2.25 | PVC
MH-10 | 583.35 | 583.35 | 581.55 | 1.2 | 1.8 | P-10 | MH-10 | MH-11 | 27.5 | 0.423 | Circular | 200 mm | 0.85 | 0.07 | 1.55 | PVC
MH-11 | 581.33 | 581.33 | 579.6 | 1.2 | 1.73 | P-11 | MH-11 | MH-12 | 32 | 1.012 | Circular | 200 mm | 0.88 | 0.035312 | 1.51 | PVC
MH-12 | 580.17 | 580.17 | 578.44 | 1.2 | 1.73 | P-12 | MH-12 | MH-13 | 37 | 1.033 | Circular | 200 mm | 0.97 | 0.046216 | 1.51 | PVC
MH-13 | 578.43 | 578.43 | 576.7 | 1.2 | 1.73 | P-13 | MH-13 | MH-14 | 47 | 1.064 | Circular | 200 mm | 0.84 | 0.03 | 1.56 | PVC
MH-14 | 577.08 | 577.08 | 575.26 | 1.2 | 1.82 | P-14 | MH-14 | MH-15 | 35 | 1.088 | Circular | 200 mm | 0.88 | 0.033429 | 1.56 | PVC
MH-15 | 575.79 | 575.79 | 574.06 | 1.2 | 1.73 | P-15 | MH-15 | MH-16 | 35 | 1.109 | Circular | 200 mm | 0.92 | 0.037714 | 1.51 | PVC
MH-16 | 574.44 | 574.44 | 572.71 | 1.2 | 1.73 | P-16 | MH-16 | MH-17 | 35 | 1.133 | Circular | 200 mm | 0.95 | 0.040571 | 1.51 | PVC
MH-17 | 572.99 | 572.99 | 571.26 | 1.2 | 1.73 | P-17 | MH-17 | MH-18 | 35 | 1.152 | Circular | 200 mm | 0.96 | 0.040286 | 1.51 | PVC
MH-18 | 571.55 | 571.55 | 569.82 | 1.2 | 1.73 | P-18 | MH-18 | MH-19 | 35 | 1.17 | Circular | 200 mm | 0.92 | 0.036 | 1.57 | PVC
MH-19 | 570.38 | 570.38 | 568.53 | 1.2 | 1.85 | P-19 | MH-19 | MH-20 | 35 | 1.192 | Circular | 200 mm | 1.04 | 0.05 | 1.57 | PVC
MH-20 | 568.48 | 568.48 | 566.75 | 1.2 | 1.73 | P-20 | MH-20 | MH-21 | 35 | 1.223 | Circular | 200 mm | 1.22 | 0.077143 | 1.51 | PVC
MH-21 | 565.75 | 565.75 | 564.02 | 1.2 | 1.73 | P-21 | MH-21 | MH-22 | 35 | 1.258 | Circular | 200 mm | 1.32 | 0.094286 | 1.51 | PVC
MH-22 | 562.42 | 562.42 | 560.69 | 1.2 | 1.73 | P-22 | MH-22 | MH-23 | 35.5 | 1.284 | Circular | 200 mm | 1.42 | 0.11521 | 1.51 | PVC
MH-23 | 558.3 | 558.3 | 556.57 | 1.2 | 1.73 | P-23 | MH-23 | MH-24 | 33 | 1.323 | Circular | 200 mm | 1.5 | 0.13061 | 1.51 | PVC
MH-24 | 553.96 | 553.96 | 552.23 | 1.2 | 1.73 | P-24 | MH-24 | MH-25 | 34 | 1.345 | Circular | 200 mm | 1.31 | 0.086765 | 1.51 | PVC
MH-25 | 550.98 | 550.98 | 549.25 | 1.2 | 1.73 | P-25 | MH-25 | MH-26 | 25.5 | 1.362 | Circular | 200 mm | 1.58 | 0.14863 | 1.51 | PVC
MH-26 | 547.16 | 547.16 | 545.43 | 1.2 | 1.73 | P-26 | MH-26 | MH-27 | 44 | 1.382 | Circular | 200 mm | 1.42 | 0.10614 | 1.51 | PVC
MH-27 | 542.46 | 542.46 | 540.73 | 1.2 | 1.73 | P-27 | MH-27 | MH-28 | 34.5 | 1.4 | Circular | 200 mm | 1.52 | 0.12783 | 1.51 | PVC
MH-28 | 538.02 | 538.02 | 536.29 | 1.2 | 1.73 | P-28 | MH-28 | MH-29 | 34.5 | 1.414 | Circular | 200 mm | 1.49 | 0.12174 | 1.51 | PVC
MH-29 | 533.79 | 533.79 | 530.82 | 1.2 | 2.97 | P-29 | MH-29 | MH-30 | 34.5 | 1.429 | Circular | 200 mm | 1.61 | 0.15 | 2.13 | PVC
MH-30 | 527.35 | 527.35 | 525.62 | 1.2 | 1.73 | P-30 | MH-30 | MH-31 | 35 | 1.444 | Circular | 200 mm | 1.35 | 0.088857 | 1.51 | PVC
MH-31 | 524.21 | 524.21 | 522.48 | 1.2 | 1.73 | P-31 | MH-31 | MH-32 | 41 | 1.457 | Circular | 200 mm | 1.05 | 0.043171 | 1.51 | PVC
MH-32 | 522.41 | 522.41 | 520.68 | 1.2 | 1.73 | P-32 | MH-32 | MH-33 | 34.5 | 1.468 | Circular | 200 mm | 1.6 | 0.14261 | 1.51 | PVC
MH-33 | 517.46 | 517.46 | 515.73 | 1.2 | 1.73 | P-33 | MH-33 | MH-34 | 34.5 | 1.487 | Circular | 200 mm | 1.57 | 0.13536 | 1.51 | PVC
MH-34 | 512.76 | 512.76 | 511.03 | 1.2 | 1.73 | P-34 | MH-34 | MH-35 | 34.5 | 1.515 | Circular | 200 mm | 1.5 | 0.11623 | 1.51 | PVC
MH-35 | 508.72 | 508.72 | 506.99 | 1.2 | 1.73 | P-35 | MH-35 | MH-36 | 34.5 | 1.551 | Circular | 200 mm | 1.5 | 0.11333 | 1.51 | PVC
MH-36 | 504.78 | 504.78 | 503.05 | 1.2 | 1.73 | P-36 | MH-36 | O-1 | 53.5 | 1.582 | Circular | 200 mm | 1.47 | 0.10467 | 1.51 | PVC
O-1 | 499.15 | 499.15 | 497.45 | 1.2 | 1.7