## Sheet1
Table ( F ) Sanitary Sewer Design Report For Al Burj village( Line F ) | [16 empty] | `
Manhole Report | [5 empty] | Pipe Report
Label | Ground Elevation (m) | Rim Elevation (m) | Sump Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (l/s) | Section Shape | Section Size | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 523.23 | 523.23 | 521.53 | 1.2 | 1.7 | P-1 | MH-1 | MH-2 | 35 | 0.022 | Circular | 200 mm | 0.21 | 0.015 | 2.25 | PVC
MH-2 | 524.2 | 524.2 | 520.97 | 1.2 | 3.23 | P-2 | MH-2 | MH-3 | 35 | 0.036 | Circular | 200 mm | 0.24 | 0.015 | 3.69 | PVC
MH-3 | 525 | 525 | 520.42 | 1.2 | 4.58 | P-3 | MH-3 | MH-4 | 35 | 0.049 | Circular | 200 mm | 0.26 | 0.015 | 4.64 | PVC
MH-4 | 525 | 525 | 519.86 | 1.2 | 5.14 | P-4 | MH-4 | MH-5 | 35 | 0.064 | Circular | 200 mm | 0.36 | 0.03 | 4.74 | PVC
MH-5 | 523.56 | 523.56 | 518.78 | 1.2 | 4.78 | P-5 | MH-5 | MH-6 | 35 | 0.075 | Circular | 200 mm | 0.38 | 0.03 | 4.04 | PVC
MH-6 | 521.43 | 521.43 | 517.7 | 1.2 | 3.73 | P-6 | MH-6 | MH-7 | 35 | 0.089 | Circular | 200 mm | 0.43 | 0.039 | 2.95 | PVC
MH-7 | 518.91 | 518.91 | 516.31 | 1.2 | 2.6 | P-7 | MH-7 | MH-8 | 35 | 0.098 | Circular | 200 mm | 0.55 | 0.07 | 1.95 | PVC
MH-8 | 515.56 | 515.56 | 513.55 | 1.2 | 2.01 | P-8 | MH-8 | MH-9 | 35 | 0.107 | Circular | 200 mm | 0.57 | 0.07 | 1.65 | PVC
MH-9 | 512.8 | 512.8 | 510.91 | 1.2 | 1.89 | P-9 | MH-9 | MH-10 | 35 | 0.116 | Circular | 200 mm | 0.58 | 0.07 | 1.59 | PVC
MH-10 | 510.16 | 510.16 | 508.43 | 1.2 | 1.73 | P-10 | MH-10 | MH-11 | 35 | 0.125 | Circular | 200 mm | 0.44 | 0.03 | 1.98 | PVC
MH-11 | 510 | 510 | 507.35 | 1.2 | 2.65 | P-11 | MH-11 | MH-12 | 35 | 0.136 | Circular | 200 mm | 0.31 | 0.01 | 2.64 | PVC
MH-12 | 510.02 | 510.02 | 506.97 | 1.2 | 3.05 | P-12 | MH-12 | MH-13 | 35 | 0.147 | Circular | 200 mm | 0.31 | 0.01 | 3.1 | PVC
MH-13 | 510.16 | 510.16 | 506.59 | 1.2 | 3.57 | P-13 | MH-13 | MH-14 | 35 | 0.16 | Circular | 200 mm | 0.32 | 0.01 | 3.61 | PVC
MH-14 | 510.29 | 510.29 | 506.21 | 1.2 | 4.08 | P-14 | MH-14 | MH-15 | 35 | 0.17 | Circular | 200 mm | 0.33 | 0.01 | 4.12 | PVC
MH-15 | 510.42 | 510.42 | 505.83 | 1.2 | 4.59 | P-15 | MH-15 | MH-16 | 35 | 0.179 | Circular | 200 mm | 0.33 | 0.01 | 4.47 | PVC
MH-16 | 510.23 | 510.23 | 505.45 | 1.2 | 4.78 | P-16 | MH-16 | MH-17 | 35 | 0.191 | Circular | 200 mm | 0.34 | 0.01 | 4.67 | PVC
MH-17 | 510.05 | 510.05 | 505.07 | 1.2 | 4.98 | P-17 | MH-17 | MH-18 | 35 | 0.21 | Circular | 200 mm | 0.35 | 0.01 | 3.36 | PVC
MH-18 | 506.86 | 506.86 | 504.69 | 1.2 | 2.17 | P-18 | MH-18 | MH-19 | 34.5 | 0.231 | Circular | 200 mm | 0.72 | 0.073333 | 1.74 | PVC
MH-19 | 503.86 | 503.86 | 502.13 | 1.2 | 1.73 | P-19 | MH-19 | MH-20 | 34.5 | 0.285 | Circular | 200 mm | 0.74 | 0.065652 | 1.59 | PVC
MH-20 | 501.71 | 501.71 | 499.83 | 1.2 | 1.88 | P-20 | MH-20 | MH-21 | 35 | 0.325 | Circular | 200 mm | 0.81 | 0.075 | 1.59 | PVC
MH-21 | 498.91 | 498.91 | 496.52 | 1.2 | 2.39 | P-21 | MH-21 | MH-22 | 34.5 | 0.363 | Circular | 200 mm | 0.83 | 0.075 | 1.84 | PVC
MH-22 | 495.64 | 495.64 | 493.91 | 1.2 | 1.73 | P-22 | MH-22 | MH-23 | 35 | 0.401 | Circular | 200 mm | 0.78 | 0.057429 | 1.51 | PVC
MH-23 | 493.6 | 493.6 | 491.87 | 1.2 | 1.73 | P-23 | MH-23 | MH-24 | 33 | 0.449 | Circular | 200 mm | 0.78 | 0.051515 | 1.51 | PVC
MH-24 | 491.87 | 491.87 | 490.14 | 1.2 | 1.73 | P-24 | MH-24 | MH-25 | 35.5 | 0.497 | Circular | 200 mm | 0.83 | 0.055563 | 1.8 | PVC
MH-25 | 490.43 | 490.43 | 488.13 | 1.2 | 2.3 | P-25 | MH-25 | MH-26 | 34.5 | 0.529 | Circular | 200 mm | 0.94 | 0.075 | 1.8 | PVC
MH-26 | 487.25 | 487.25 | 485.52 | 1.2 | 1.73 | P-26 | MH-26 | MH-27 | 38 | 0.557 | Circular | 200 mm | 1.2 | 0.14605 | 1.51 | PVC
MH-27 | 481.67 | 481.67 | 479.94 | 1.2 | 1.73 | P-27 | MH-27 | MH-28 | 31.5 | 0.571 | Circular | 200 mm | 1.12 | 0.11936 | 1.51 | PVC
MH-28 | 477.88 | 477.88 | 476.15 | 1.2 | 1.73 | P-28 | MH-28 | MH-29 | 35 | 0.589 | Circular | 200 mm | 1.05 | 0.095143 | 1.51 | PVC
MH-29 | 474.52 | 474.52 | 472.79 | 1.2 | 1.73 | P-29 | MH-29 | MH-30 | 34.5 | 0.607 | Circular | 200 mm | 0.62 | 0.02 | 1.51 | PVC
MH-30 | 473.8 | 473.8 | 472.07 | 1.2 | 1.73 | P-30 | MH-30 | MH-31 | 33 | 0.627 | Circular | 200 mm | 0.61 | 0.018788 | 1.51 | PVC
MH-31 | 473.15 | 473.15 | 471.42 | 1.2 | 1.73 | P-31 | MH-31 | MH-32 | 34.5 | 0.647 | Circular | 200 mm | 0.64 | 0.02087 | 1.51 | PVC
MH-32 | 472.4 | 472.4 | 470.67 | 1.2 | 1.73 | P-32 | MH-32 | MH-33 | 35 | 0.683 | Circular | 200 mm | 0.63 | 0.018857 | 1.51 | PVC
MH-33 | 471.71 | 471.71 | 469.98 | 1.2 | 1.73 | P-33 | MH-33 | MH-34 | 35 | 0.717 | Circular | 200 mm | 0.64 | 0.019143 | 1.51 | PVC
MH-34 | 471.01 | 471.01 | 469.28 | 1.2 | 1.73 | P-34 | MH-34 | MH-35 | 35 | 0.743 | Circular | 200 mm | 0.64 | 0.018857 | 1.51 | PVC
MH-35 | 470.32 | 470.32 | 468.59 | 1.2 | 1.73 | P-35 | MH-35 | MH-36 | 34.5 | 0.765 | Circular | 200 mm | 1.02 | 0.068696 | 1.51 | PVC
MH-36 | 467.92 | 467.92 | 466.19 | 1.2 | 1.73 | P-36 | MH-36 | MH-37 | 37 | 0.783 | Circular | 200 mm | 1.24 | 0.11351 | 1.56 | PVC
MH-37 | 463.78 | 463.78 | 461.96 | 1.2 | 1.82 | P-37 | MH-37 | MH-38 | 34 | 0.805 | Circular | 200 mm | 1.37 | 0.15 | 1.56 | PVC
MH-38 | 458.56 | 458.56 | 456.18 | 1.2 | 2.38 | P-38 | MH-38 | MH-39 | 35 | 0.841 | Circular | 200 mm | 1.38 | 0.15 | 1.84 | PVC
MH-39 | 452.63 | 452.63 | 450.41 | 1.2 | 2.22 | P-39 | MH-39 | MH-40 | 34.5 | 0.881 | Circular | 200 mm | 1.41 | 0.15 | 1.76 | PVC
MH-40 | 446.94 | 446.94 | 443.95 | 1.2 | 2.99 | P-40 | MH-40 | MH-41 | 34.5 | 0.921 | Circular | 200 mm | 1.41 | 0.15 | 2.14 | PVC
MH-41 | 440.48 | 440.48 | 437.09 | 1.2 | 3.39 | P-41 | MH-41 | MH-42 | 34 | 1.006 | Circular | 200 mm | 1.45 | 0.15 | 2.34 | PVC
MH-42 | 433.69 | 433.69 | 431.96 | 1.2 | 1.73 | P-42 | MH-42 | MH-43 | 34.5 | 1.08 | Circular | 200 mm | 1.31 | 0.10609 | 1.51 | PVC
MH-43 | 430 | 430 | 428.27 | 1.2 | 1.73 | P-43 | MH-43 | MH-44 | 34.5 | 1.096 | Circular | 200 mm | 0.6 | 0.011104 | 1.72 | PVC
MH-44 | 430 | 430 | 427.85 | 1.2 | 2.15 | P-44 | MH-44 | O-1 | 39 | 1.124 | Circular | 200 mm | 0.6 | 0.010865 | 2.24 | PVC
O-1 | 430.17 | 430.17 | 427.43 | 1.2 | 2.74