## Sheet1
Table ( G ) Sanitary Sewer Design Report For Al Burj village( Line G ) | [16 empty] | `
Manhole Report | [5 empty] | Pipe Report
Label | Ground Elevation (m) | Rim Elevation (m) | Sump Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (l/s) | Section Shape | Section Size | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 503.45 | 503.45 | 501.75 | 1.2 | 1.7 | P-1 | MH-1 | MH-2 | 35 | 1.226 | Circular | 200 mm | 1 | 0.044 | 1.5 | PVC
MH-2 | 501.91 | 501.91 | 500.18 | 1.2 | 1.73 | P-2 | MH-2 | MH-3 | 35 | 1.354 | Circular | 200 mm | 1.07 | 0.048714 | 1.61 | PVC
MH-3 | 500.37 | 500.37 | 498.44 | 1.2 | 1.93 | P-3 | MH-3 | MH-4 | 34.5 | 1.499 | Circular | 200 mm | 1.64 | 0.15 | 1.61 | PVC
MH-4 | 494.97 | 494.97 | 493.24 | 1.2 | 1.73 | P-4 | MH-4 | MH-5 | 35 | 1.621 | Circular | 200 mm | 0.96 | 0.030286 | 1.51 | PVC
MH-5 | 493.88 | 493.88 | 492.15 | 1.2 | 1.73 | P-5 | MH-5 | MH-6 | 35 | 1.73 | Circular | 200 mm | 0.97 | 0.03 | 1.51 | PVC
MH-6 | 492.8 | 492.8 | 491.07 | 1.2 | 1.73 | P-6 | MH-6 | MH-7 | 35 | 1.85 | Circular | 200 mm | 0.99 | 0.03 | 1.51 | PVC
MH-7 | 491.72 | 491.72 | 489.99 | 1.2 | 1.73 | P-7 | MH-7 | MH-8 | 35 | 1.964 | Circular | 200 mm | 1.02 | 0.030286 | 1.51 | PVC
MH-8 | 490.63 | 490.63 | 488.9 | 1.2 | 1.73 | P-8 | MH-8 | MH-9 | 34.5 | 2.054 | Circular | 200 mm | 1.66 | 0.11841 | 1.95 | PVC
MH-9 | 487.39 | 487.39 | 484.78 | 1.2 | 2.61 | P-9 | MH-9 | MH-10 | 34.5 | 2.151 | Circular | 200 mm | 1.83 | 0.15 | 1.95 | PVC
MH-10 | 481.31 | 481.31 | 479.58 | 1.2 | 1.73 | P-10 | MH-10 | MH-11 | 34.5 | 2.237 | Circular | 200 mm | 1.42 | 0.071304 | 1.51 | PVC
MH-11 | 478.82 | 478.82 | 477.09 | 1.2 | 1.73 | P-11 | MH-11 | MH-12 | 35 | 2.332 | Circular | 200 mm | 1.2 | 0.042 | 1.51 | PVC
MH-12 | 477.32 | 477.32 | 475.59 | 1.2 | 1.73 | P-12 | MH-12 | MH-13 | 35 | 2.408 | Circular | 200 mm | 1.21 | 0.042 | 1.51 | PVC
MH-13 | 475.82 | 475.82 | 474.09 | 1.2 | 1.73 | P-13 | MH-13 | MH-14 | 35 | 2.5 | Circular | 200 mm | 1.64 | 0.097286 | 1.66 | PVC
MH-14 | 472.67 | 472.67 | 470.65 | 1.2 | 2.02 | P-14 | MH-14 | MH-15 | 34.5 | 2.597 | Circular | 200 mm | 1.93 | 0.15 | 1.66 | PVC
MH-15 | 467.18 | 467.18 | 465.45 | 1.2 | 1.73 | P-15 | MH-15 | MH-16 | 35 | 2.68 | Circular | 200 mm | 1.61 | 0.086571 | 1.51 | PVC
MH-16 | 464.12 | 464.12 | 462.39 | 1.2 | 1.73 | P-16 | MH-16 | MH-17 | 35 | 2.801 | Circular | 200 mm | 1.24 | 0.039143 | 1.51 | PVC
MH-17 | 462.72 | 462.72 | 460.99 | 1.2 | 1.73 | P-17 | MH-17 | MH-18 | 35 | 2.934 | Circular | 200 mm | 1.25 | 0.039143 | 1.51 | PVC
MH-18 | 461.32 | 461.32 | 459.59 | 1.2 | 1.73 | P-18 | MH-18 | MH-19 | 35 | 3.053 | Circular | 200 mm | 1.28 | 0.040286 | 1.51 | PVC
MH-19 | 459.88 | 459.88 | 458.15 | 1.2 | 1.73 | P-19 | MH-19 | MH-20 | 35 | 3.154 | Circular | 200 mm | 1.49 | 0.059143 | 1.51 | PVC
MH-20 | 457.78 | 457.78 | 456.05 | 1.2 | 1.73 | P-20 | MH-20 | MH-21 | 35 | 3.273 | Circular | 200 mm | 1.5 | 0.059143 | 1.51 | PVC
MH-21 | 455.68 | 455.68 | 453.95 | 1.2 | 1.73 | P-21 | MH-21 | MH-22 | 34.5 | 3.389 | Circular | 200 mm | 2.09 | 0.14927 | 1.51 | PVC
MH-22 | 450.5 | 450.5 | 448.77 | 1.2 | 1.73 | P-22 | MH-22 | MH-23 | 35 | 3.517 | Circular | 200 mm | 1.56 | 0.062571 | 1.51 | PVC
MH-23 | 448.28 | 448.28 | 446.55 | 1.2 | 1.73 | P-23 | MH-23 | MH-24 | 35 | 3.628 | Circular | 200 mm | 1.48 | 0.052286 | 1.51 | PVC
MH-24 | 446.42 | 446.42 | 444.69 | 1.2 | 1.73 | P-24 | MH-24 | MH-25 | 35 | 3.737 | Circular | 200 mm | 1.52 | 0.054857 | 1.51 | PVC
MH-25 | 444.47 | 444.47 | 442.74 | 1.2 | 1.73 | P-25 | MH-25 | MH-26 | 35 | 3.844 | Circular | 200 mm | 1.62 | 0.064571 | 1.51 | PVC
MH-26 | 442.18 | 442.18 | 440.45 | 1.2 | 1.73 | P-26 | MH-26 | MH-27 | 35 | 4.052 | Circular | 200 mm | 1.65 | 0.065143 | 1.51 | PVC
MH-27 | 439.87 | 439.87 | 438.14 | 1.2 | 1.73 | P-27 | MH-27 | MH-28 | 35 | 4.132 | Circular | 200 mm | 1.79 | 0.081143 | 1.51 | PVC
MH-28 | 437 | 437 | 435.27 | 1.2 | 1.73 | P-28 | MH-28 | MH-29 | 35 | 4.663 | Circular | 200 mm | 1.76 | 0.069143 | 1.51 | PVC
MH-29 | 434.55 | 434.55 | 432.82 | 1.2 | 1.73 | P-29 | MH-29 | MH-30 | 35 | 4.753 | Circular | 200 mm | 1.47 | 0.040857 | 1.51 | PVC
MH-30 | 433.09 | 433.09 | 431.36 | 1.2 | 1.73 | P-30 | MH-30 | MH-31 | 35 | 4.85 | Circular | 200 mm | 1.48 | 0.041143 | 1.51 | PVC
MH-31 | 431.62 | 431.62 | 429.89 | 1.2 | 1.73 | P-31 | MH-31 | MH-32 | 35 | 4.927 | Circular | 200 mm | 1.48 | 0.040857 | 1.51 | PVC
MH-32 | 430.16 | 430.16 | 428.43 | 1.2 | 1.73 | P-32 | MH-32 | MH-33 | 35 | 5.036 | Circular | 200 mm | 1.69 | 0.058 | 1.51 | PVC
MH-33 | 428.1 | 428.1 | 426.37 | 1.2 | 1.73 | P-33 | MH-33 | MH-34 | 35 | 5.13 | Circular | 200 mm | 1.72 | 0.06 | 1.51 | PVC
MH-34 | 425.97 | 425.97 | 424.24 | 1.2 | 1.73 | P-34 | MH-34 | MH-35 | 34 | 5.22 | Circular | 200 mm | 1.55 | 0.044118 | 1.51 | PVC
MH-35 | 424.44 | 424.44 | 422.71 | 1.2 | 1.73 | P-35 | MH-35 | MH-36 | 35 | 5.274 | Circular | 200 mm | 1.33 | 0.028 | 1.51 | PVC
MH-36 | 423.43 | 423.43 | 421.7 | 1.2 | 1.73 | P-36 | MH-36 | MH-37 | 35 | 5.345 | Circular | 200 mm | 1.34 | 0.028286 | 1.51 | PVC
MH-37 | 422.41 | 422.41 | 420.68 | 1.2 | 1.73 | P-37 | MH-37 | MH-38 | 35 | 5.391 | Circular | 200 mm | 1.34 | 0.028286 | 1.51 | PVC
MH-38 | 421.39 | 421.39 | 419.66 | 1.2 | 1.73 | P-38 | MH-38 | MH-39 | 35 | 5.435 | Circular | 200 mm | 1.34 | 0.028 | 1.51 | PVC
MH-39 | 420.38 | 420.38 | 418.65 | 1.2 | 1.73 | P-39 | MH-39 | MH-40 | 32.5 | 5.472 | Circular | 200 mm | 0.96 | 0.010769 | 1.51 | PVC
MH-40 | 420 | 420 | 418.27 | 1.2 | 1.73 | P-40 | MH-40 | O-1 | 41.5 | 7.971 | Circular | 200 mm | 0.81 | 0.005 | 1.63 | PVC
O-1 | 420 | 420 | 418.06 | 1.2 | 1.94