## Sheet1
Table ( A ) Sanitary Sewer Design Report For Al Burj village( Line A )
Manhole Report | [5 empty] | Pipe Report
Label | Ground Elevation (m) | Rim Elevation (m) | Sump Elevation (m) | Manhole Diameter (m) | Manhole Depth (m) | Label | Upstream Manhole | Downstream Manhole | Length (m) | Total Flow (l/s) | Section Shape | Section Size | Average Velocity (m/s) | Constructed Slope (m/m) | Average Pipe Cover (m) | Material
MH-1 | 500 | 500 | 498.3 | 1.2 | 1.7 | P-1 | MH-1 | MH-2 | 34.5 | 0.044 | Circular | 200 mm | 1.74 | 0.13916 | 1.5 | PVC
MH-2 | 495.2 | 495.2 | 493.47 | 1.2 | 1.73 | P-2 | MH-2 | MH-3 | 35 | 0.06 | Circular | 200 mm | 0.38 | 0.038286 | 1.51 | PVC
MH-3 | 493.83 | 493.83 | 492.1 | 1.2 | 1.73 | P-3 | MH-3 | MH-4 | 35 | 0.077 | Circular | 200 mm | 0.4 | 0.034257 | 1.51 | PVC
MH-4 | 492.6 | 492.6 | 490.87 | 1.2 | 1.73 | P-4 | MH-4 | MH-5 | 35 | 0.092 | Circular | 200 mm | 0.42 | 0.0338 | 1.51 | PVC
MH-5 | 491.39 | 491.39 | 489.65 | 1.2 | 1.74 | P-5 | MH-5 | MH-6 | 35 | 0.106 | Circular | 200 mm | 0.44 | 0.034057 | 1.51 | PVC
MH-6 | 490.17 | 490.17 | 488.43 | 1.2 | 1.74 | P-6 | MH-6 | MH-7 | 35 | 0.118 | Circular | 200 mm | 0.46 | 0.0368 | 1.51 | PVC
MH-7 | 488.85 | 488.85 | 487.11 | 1.2 | 1.74 | P-7 | MH-7 | MH-8 | 35 | 0.119 | Circular | 200 mm | 0.47 | 0.037229 | 1.51 | PVC
MH-8 | 487.51 | 487.51 | 485.78 | 1.2 | 1.73 | P-8 | MH-8 | MH-9 | 35 | 0.137 | Circular | 200 mm | 0.49 | 0.037257 | 1.51 | PVC
MH-9 | 486.18 | 486.18 | 484.45 | 1.2 | 1.73 | P-9 | MH-9 | MH-10 | 35 | 0.152 | Circular | 200 mm | 0.6 | 0.062497 | 1.58 | PVC
MH-10 | 484.09 | 484.09 | 482.23 | 1.2 | 1.86 | P-10 | MH-10 | MH-11 | 34.5 | 0.175 | Circular | 200 mm | 0.82 | 0.13602 | 1.58 | PVC
MH-11 | 479.24 | 479.24 | 477.51 | 1.2 | 1.73 | P-11 | MH-11 | MH-12 | 35 | 0.187 | Circular | 200 mm | 0.6 | 0.052053 | 1.66 | PVC
MH-12 | 477.67 | 477.67 | 475.65 | 1.2 | 2.02 | P-12 | MH-12 | MH-13 | 35 | 0.206 | Circular | 200 mm | 0.6 | 0.0478 | 1.87 | PVC
MH-13 | 476.11 | 476.11 | 473.95 | 1.2 | 2.16 | P-13 | MH-13 | MH-14 | 34.5 | 0.229 | Circular | 200 mm | 0.6 | 0.043546 | 1.86 | PVC
MH-14 | 474.43 | 474.43 | 472.42 | 1.2 | 2.01 | P-14 | MH-14 | MH-15 | 35 | 0.244 | Circular | 200 mm | 0.63 | 0.046766 | 1.65 | PVC
MH-15 | 472.49 | 472.49 | 470.75 | 1.2 | 1.74 | P-15 | MH-15 | MH-16 | 35 | 0.264 | Circular | 200 mm | 0.68 | 0.054629 | 1.51 | PVC
MH-16 | 470.54 | 470.54 | 468.81 | 1.2 | 1.73 | P-16 | MH-16 | MH-17 | 35 | 0.282 | Circular | 200 mm | 0.88 | 0.11237 | 1.51 | PVC
MH-17 | 466.58 | 466.58 | 464.85 | 1.2 | 1.73 | P-17 | MH-17 | MH-18 | 35 | 0.321 | Circular | 200 mm | 0.67 | 0.044314 | 1.51 | PVC
MH-18 | 465 | 465 | 463.27 | 1.2 | 1.73 | P-18 | MH-18 | MH-19 | 35 | 0.336 | Circular | 200 mm | 0.6 | 0.03109 | 2.07 | PVC
MH-19 | 465 | 465 | 462.15 | 1.2 | 2.85 | P-19 | MH-19 | MH-20 | 35 | 0.348 | Circular | 200 mm | 0.6 | 0.030147 | 3.18 | PVC
MH-20 | 465 | 465 | 461.06 | 1.2 | 3.94 | P-20 | MH-20 | MH-21 | 35 | 0.362 | Circular | 200 mm | 0.6 | 0.029123 | 4.24 | PVC
MH-21 | 465 | 465 | 460.01 | 1.2 | 4.99 | P-21 | MH-21 | MH-22 | 35 | 0.379 | Circular | 200 mm | 0.61 | 0.027973 | 4.03 | PVC
MH-22 | 462.52 | 462.52 | 459.01 | 1.2 | 3.51 | P-22 | MH-22 | MH-23 | 35 | 0.394 | Circular | 200 mm | 0.6 | 0.027039 | 2.52 | PVC
MH-23 | 460 | 460 | 458.03 | 1.2 | 1.97 | P-23 | MH-23 | MH-24 | 35 | 0.409 | Circular | 200 mm | 0.84 | 0.069056 | 1.64 | PVC
MH-24 | 457.33 | 457.33 | 455.58 | 1.2 | 1.75 | P-24 | MH-24 | MH-25 | 35 | 0.424 | Circular | 200 mm | 0.85 | 0.07 | 1.52 | PVC
MH-25 | 454.84 | 454.84 | 452.95 | 1.2 | 1.89 | P-25 | MH-25 | MH-26 | 35 | 0.439 | Circular | 200 mm | 0.64 | 0.03 | 1.59 | PVC
MH-26 | 453.61 | 453.61 | 451.72 | 1.2 | 1.89 | P-26 | MH-26 | MH-27 | 35 | 0.456 | Circular | 200 mm | 0.65 | 0.03 | 1.59 | PVC
MH-27 | 452.38 | 452.38 | 450.49 | 1.2 | 1.89 | P-27 | MH-27 | MH-28 | 35 | 0.474 | Circular | 200 mm | 0.66 | 0.03 | 1.59 | PVC
MH-28 | 451.15 | 451.15 | 449.16 | 1.2 | 1.99 | P-28 | MH-28 | MH-29 | 35 | 0.489 | Circular | 200 mm | 0.66 | 0.03 | 1.64 | PVC
MH-29 | 449.81 | 449.81 | 448.08 | 1.2 | 1.73 | P-29 | MH-29 | MH-30 | 35 | 0.506 | Circular | 200 mm | 0.94 | 0.079971 | 1.51 | PVC
MH-30 | 446.98 | 446.98 | 445.25 | 1.2 | 1.73 | P-30 | MH-30 | MH-31 | 35 | 0.519 | Circular | 200 mm | 1.05 | 0.10586 | 1.59 | PVC
MH-31 | 443.4 | 443.4 | 441.51 | 1.2 | 1.89 | P-31 | MH-31 | MH-32 | 35 | 0.533 | Circular | 200 mm | 0.68 | 0.03 | 1.59 | PVC
MH-32 | 442.17 | 442.17 | 440.28 | 1.2 | 1.89 | P-32 | MH-32 | MH-33 | 35 | 0.545 | Circular | 200 mm | 0.69 | 0.03 | 1.59 | PVC
MH-33 | 440.93 | 440.93 | 439.2 | 1.2 | 1.73 | P-33 | MH-33 | MH-34 | 35 | 0.561 | Circular | 200 mm | 0.6 | 0.019853 | 1.88 | PVC
MH-34 | 440.93 | 440.93 | 438.47 | 1.2 | 2.46 | P-34 | MH-34 | MH-35 | 35 | 0.575 | Circular | 200 mm | 0.67 | 0.026804 | 2.08 | PVC
MH-35 | 439.64 | 439.64 | 437.51 | 1.2 | 2.13 | P-35 | MH-35 | MH-36 | 35 | 0.587 | Circular | 200 mm | 0.7 | 0.03 | 1.71 | PVC
MH-36 | 438.16 | 438.16 | 436.03 | 1.2 | 2.13 | P-36 | MH-36 | MH-37 | 35 | 0.596 | Circular | 200 mm | 0.71 | 0.03 | 1.71 | PVC
MH-37 | 436.68 | 436.68 | 434.54 | 1.2 | 2.14 | P-37 | MH-37 | MH-38 | 35 | 0.606 | Circular | 200 mm | 0.71 | 0.03 | 1.72 | PVC
MH-38 | 435.2 | 435.2 | 433.44 | 1.2 | 1.76 | P-38 | MH-38 | MH-39 | 33.5 | 0.614 | Circular | 200 mm | 0.71 | 0.03 | 1.53 | PVC
MH-39 | 434.14 | 434.14 | 432.41 | 1.2 | 1.73 | P-39 | MH-39 | MH-40 | 35 | 0.626 | Circular | 200 mm | 0.69 | 0.027486 | 1.51 | PVC
MH-40 | 433.15 | 433.15 | 431.41 | 1.2 | 1.74 | P-40 | MH-40 | MH-41 | 35 | 0.634 | Circular | 200 mm | 0.7 | 0.027514 | 1.51 | PVC
MH-41 | 432.15 | 432.15 | 430.42 | 1.2 | 1.73 | P-41 | MH-41 | MH-42 | 35 | 0.642 | Circular | 200 mm | 0.7 | 0.027486 | 1.51 | PVC
MH-42 | 431.16 | 431.16 | 429.43 | 1.2 | 1.73 | P-42 | MH-42 | O-1 | 35 | 0.65 | Circular | 200 mm | 0.7 | 0.027514 | 1.51 | PVC
O-1 | 430.17 | 430.17 | 428.47 | 1.2 | 1.7